## Basis (hidden)
Selection Model 2022-10 |  | LA/2022-10-12 |  | 2 |  | Vul in: 1 voor Metric en 2 voor Imperial
Metric | BTU/h | 1 | 3.4121 | 3.4121
Imperial | INCH | 1 | 2.54 | 2.54 |  |  | Altitude dynamics
| CFM | 1 | 0.58857 | 0.58857 |  |  | 0 | 1 | 609.9048 | 2001
| GPM | 1 | 0.004403 | 0.004403 |  |  | 3001 | 0.96 | 914.7048 | 3001
| P_loss | 1 | 4.0147 | 4.0147 |  |  | 4001 | 0.92 | 1219.5048 | 4001
heating | ref | 49.8329 | 89.6992 | 89.6992 |  |  | 5001 | 0.84 | 1524.3048 | 5001
cooling | ref | -9.9666 | -18.4594 | -18.4594 |  |  | 6001 | 0.8 | 1829.1048 | 6001
in->ft |  | 1 | 12 | 12 |  |  | 7001 | 0.76 | 2133.9048 | 7001
LowH2O drop | ftH2O | 1 | 2.997 | 2.997 | correctie mbv DoelZoeken |  | 8001 | 0.72 | 2438.7048 | 8001
cm->m |  | 100 | 1 | 1
| CFMs | 0.58857 | 1 | 1
conversie kg/s |  | 0.00033444 | 0.00056822 | 0.00056822
factor outletº |  | 1 | 1.8 | 1.8 |  |  | Altitude LowH2O
factor outletº |  | 0 | 32 | 32 |  |  | 0 | 1 | 0 | 0
cf_H_Q |  | 5% | 5% | 5% |  |  | 8001 | 0.93 | 2438.7048 | 8001
cf_H_QcTot |  | 0.001 | 0.0003048 | 0.0003048 |  |  | 9001 | 0.91 | 2743.5048 | 9001
Cubics |  | 1 | 0.58857 | 0.58857 |  |  | 10001 | 0.89 | 3048.3048 | 10001
Feetmins |  | 1 | 196.8504 | 196.8504
Let op:
Tabbladen hebben verschillende rekenmethodes/formules | [6 empty] | Fresh Water | Eth. Glycol | Prop. Glycol
0-8000ft, no derate. | [5 empty] | 0 | 1 | 1 | 1
8001ft to 9000ft = 7% less BTU | [5 empty] | 20 | 1 | 0.95 | 0.98
9001ft to 10000ft = 9% less BTU |  |  |  | Fresh Water |  | 30 | 1 | 0.91 | 0.96
10001ft and above = 11% less BTU |  |  |  | Eth. Glycol |  | 40 | 1 | 0.88 | 0.93
|  |  |  | Prop. Glycol |  | 50 | 1 | 0.84 | 0.9
heating |  | cooling
min EnteringT | 89 | min EnteringT | 41

## LowH2O Convectors
Selection Model 2022-10 | [37 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF | [28 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF | [14 empty] | h(mm) | 0 | [12 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF | [14 empty] | cf_h | 1 | [12 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF | [29 empty] | -10
[11 empty] | *Sound pressure with an assumed room damping of 8dB(A) | [27 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º |  |  |  |  | N-Waarde |  | 75/65/20ºC |  | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  |  |  | 16/18/27ºC
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | BTU/h per foot | Flow in GPM | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | Kolom | 100% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | k1 | n | t | k2 | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | SalesGroup | JagaSourceCode Stnd
Build-In | Build-In Wall | BIWW.02004010 | 8 | 15.5 | 10 | 4.6 | 561 | 427 | 0.06 | 0.00028475 |  | 1.413 |  | 262 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02004015 | 8 | 15.5 | 15 | 6.6 | 935 | 712 | 0.09 | 0.00069432 |  | 1.408 |  | 436 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02004020 | 8 | 15.5 | 20 | 8.6 | 1314 | 1001 | 0.13 | 0.0011462 |  | 1.408 |  | 613 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02005010 | 8 | 19.5 | 10 | 4.6 | 702 | 428 | 0.07 | 0.00041569 |  | 1.413 |  | 328 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02005015 | 8 | 19.5 | 15 | 6.6 | 1168 | 712 | 0.12 | 0.0012664 |  | 1.408 |  | 545 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02005020 | 8 | 19.5 | 20 | 8.6 | 1642 | 1001 | 0.16 | 0.0017706 |  | 1.408 |  | 766 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02006010 | 8 | 23.5 | 10 | 4.6 | 841 | 427 | 0.08 | 0.00057754 |  | 1.413 |  | 393 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02006015 | 8 | 23.5 | 15 | 6.6 | 1402 | 712 | 0.14 | 0.0017685 |  | 1.408 |  | 654 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02006020 | 8 | 23.5 | 20 | 8.6 | 1970 | 1001 | 0.2 | 0.0028126 |  | 1.408 |  | 919 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02007010 | 8 | 27.5 | 10 | 4.6 | 982 | 428 | 0.1 | 0.0009446 |  | 1.413 |  | 459 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02007015 | 8 | 27.5 | 15 | 6.6 | 1636 | 712 | 0.16 | 0.0023652 |  | 1.408 |  | 763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02007020 | 8 | 27.5 | 20 | 8.6 | 2298 | 1001 | 0.23 | 0.0037818 |  | 1.408 |  | 1072 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02008010 | 8 | 31.5 | 10 | 4.6 | 1122 | 427 | 0.11 | 0.0012021 |  | 1.413 |  | 524 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02008015 | 8 | 31.5 | 15 | 6.6 | 1869 | 712 | 0.19 | 0.0034008 |  | 1.408 |  | 872 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02008020 | 8 | 31.5 | 20 | 8.6 | 2628 | 1001 | 0.26 | 0.0049082 |  | 1.408 |  | 1226 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02009010 | 8 | 35.5 | 10 | 4.6 | 1263 | 428 | 0.13 | 0.0017437 |  | 1.413 |  | 590 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02009015 | 8 | 35.5 | 15 | 6.6 | 2103 | 712 | 0.21 | 0.0042415 |  | 1.408 |  | 981 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02009020 | 8 | 35.5 | 20 | 8.6 | 2956 | 1001 | 0.3 | 0.0066224 |  | 1.408 |  | 1379 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02010010 | 8 | 39.5 | 10 | 4.6 | 1402 | 427 | 0.14 | 0.0021113 |  | 1.413 |  | 655 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02010015 | 8 | 39.5 | 15 | 6.6 | 2337 | 712 | 0.23 | 0.0051886 |  | 1.408 |  | 1090 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02010020 | 8 | 39.5 | 20 | 8.6 | 3284 | 1001 | 0.33 | 0.0081256 |  | 1.408 |  | 1532 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02011010 | 8 | 43.5 | 10 | 4.6 | 1543 | 428 | 0.15 | 0.0025231 |  | 1.413 |  | 721 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02011015 | 8 | 43.5 | 15 | 6.6 | 2571 | 712 | 0.26 | 0.0067392 |  | 1.408 |  | 1199 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02011020 | 8 | 43.5 | 20 | 8.6 | 3613 | 1001 | 0.36 | 0.0097997 |  | 1.408 |  | 1685 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02012010 | 8 | 47 | 10 | 4.6 | 1682 | 427 | 0.17 | 0.0033402 |  | 1.413 |  | 786 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02012015 | 8 | 47 | 15 | 6.6 | 2804 | 712 | 0.28 | 0.0079564 |  | 1.408 |  | 1308 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02012020 | 8 | 47 | 20 | 8.6 | 3941 | 1001 | 0.39 | 0.011649 |  | 1.408 |  | 1838 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02014010 | 8 | 55 | 10 | 4.6 | 1963 | 427 | 0.2 | 0.0049216 |  | 1.413 |  | 917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02014015 | 8 | 55 | 15 | 6.6 | 3272 | 712 | 0.33 | 0.011403 |  | 1.408 |  | 1526 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02014020 | 8 | 55 | 20 | 8.6 | 4599 | 1001 | 0.46 | 0.016582 |  | 1.408 |  | 2145 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02016010 | 8 | 63 | 10 | 4.6 | 2243 | 427 | 0.22 | 0.0063403 |  | 1.413 |  | 1048 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02016015 | 8 | 63 | 15 | 6.6 | 3739 | 712 | 0.37 | 0.014787 |  | 1.408 |  | 1744 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02016020 | 8 | 63 | 20 | 8.6 | 5255 | 1001 | 0.53 | 0.022489 |  | 1.408 |  | 2451 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02018010 | 8 | 71 | 10 | 4.6 | 2524 | 427 | 0.25 | 0.0086163 |  | 1.413 |  | 1179 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02018015 | 8 | 71 | 15 | 6.6 | 4206 | 712 | 0.42 | 0.019575 |  | 1.408 |  | 1962 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02018020 | 8 | 71 | 20 | 8.6 | 5913 | 1001 | 0.59 | 0.028468 |  | 1.408 |  | 2758 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02020010 | 8 | 78.5 | 10 | 4.6 | 2804 | 427 | 0.28 | 0.011329 |  | 1.413 |  | 1310 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02020015 | 8 | 78.5 | 15 | 6.6 | 4674 | 712 | 0.47 | 0.025145 |  | 1.408 |  | 2180 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02020020 | 8 | 78.5 | 20 | 8.6 | 6569 | 1001 | 0.66 | 0.03631 |  | 1.408 |  | 3064 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02022010 | 8 | 86.5 | 10 | 4.6 | 3084 | 427 | 0.31 | 0.014508 |  | 1.413 |  | 1441 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02022015 | 8 | 86.5 | 15 | 6.6 | 5141 | 712 | 0.51 | 0.030384 |  | 1.408 |  | 2398 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02022020 | 8 | 86.5 | 20 | 8.6 | 7225 | 1001 | 0.72 | 0.044048 |  | 1.408 |  | 3370 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02024010 | 8 | 94.5 | 10 | 4.6 | 3365 | 427 | 0.34 | 0.018179 |  | 1.413 |  | 1572 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02024015 | 8 | 94.5 | 15 | 6.6 | 5608 | 712 | 0.56 | 0.03748 |  | 1.408 |  | 2616 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02024020 | 8 | 94.5 | 20 | 8.6 | 7883 | 1001 | 0.79 | 0.053957 |  | 1.408 |  | 3677 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02026010 | 8 | 102.5 | 10 | 4.6 | 3645 | 427 | 0.36 | 0.021273 |  | 1.413 |  | 1703 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02026015 | 8 | 102.5 | 15 | 6.6 | 6076 | 712 | 0.61 | 0.045451 |  | 1.408 |  | 2834 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02026020 | 8 | 102.5 | 20 | 8.6 | 8539 | 1001 | 0.85 | 0.06357 |  | 1.408 |  | 3983 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02028010 | 8 | 110 | 10 | 4.6 | 3925 | 427 | 0.39 | 0.025879 |  | 1.413 |  | 1834 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02028015 | 8 | 110 | 15 | 6.6 | 6543 | 712 | 0.65 | 0.052778 |  | 1.408 |  | 3052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02028020 | 8 | 110 | 20 | 8.6 | 9197 | 1001 | 0.92 | 0.07567 |  | 1.408 |  | 4290 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.02030010 | 8 | 118 | 10 | 4.6 | 4206 | 427 | 0.42 | 0.031051 |  | 1.413 |  | 1965 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.02030015 | 8 | 118 | 15 | 6.6 | 7011 | 712 | 0.7 | 0.062443 |  | 1.408 |  | 3270 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.02030020 | 8 | 118 | 20 | 8.6 | 9853 | 1001 | 0.99 | 0.088982 |  | 1.408 |  | 4596 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03004010 | 12 | 15.5 | 10 | 4.6 | 709 | 540 | 0.07 | 0.00038421 |  | 1.403 |  | 330 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03004011 | 12 | 15.5 | 11 | 4.6 | 950 | 724 | 0.1 | 0.0012679 |  | 1.44 |  | 448 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03004015 | 12 | 15.5 | 15 | 6.6 | 1171 | 892 | 0.12 | 0.0012257 |  | 1.396 |  | 544 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03004016 | 12 | 15.5 | 16 | 6.6 | 1249 | 952 | 0.12 | 0.003591 |  | 1.456 |  | 592 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03004020 | 12 | 15.5 | 20 | 8.6 | 1640 | 1250 | 0.16 | 0.0017301 |  | 1.396 |  | 762 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03004021 | 12 | 15.5 | 21 | 8.6 | 1637 | 1247 | 0.16 | 0.002428 |  | 1.468 |  | 779 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03005010 | 12 | 19.5 | 10 | 4.6 | 887 | 541 | 0.09 | 0.00067521 |  | 1.403 |  | 413 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03005011 | 12 | 19.5 | 11 | 4.6 | 1190 | 725 | 0.12 | 0.0019658 |  | 1.44 |  | 561 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03005015 | 12 | 19.5 | 15 | 6.6 | 1464 | 892 | 0.15 | 0.0019652 |  | 1.396 |  | 680 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03005016 | 12 | 19.5 | 16 | 6.6 | 1562 | 952 | 0.16 | 0.0064892 |  | 1.456 |  | 740 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03005020 | 12 | 19.5 | 20 | 8.6 | 2051 | 1250 | 0.21 | 0.0030321 |  | 1.396 |  | 953 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03005021 | 12 | 19.5 | 21 | 8.6 | 2047 | 1248 | 0.2 | 0.0038934 |  | 1.468 |  | 974 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03006010 | 12 | 23.5 | 10 | 4.6 | 1065 | 541 | 0.11 | 0.0010642 |  | 1.403 |  | 496 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03006011 | 12 | 23.5 | 11 | 4.6 | 1428 | 725 | 0.14 | 0.0028541 |  | 1.44 |  | 673 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03006015 | 12 | 23.5 | 15 | 6.6 | 1754 | 891 | 0.18 | 0.0028967 |  | 1.396 |  | 815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03006016 | 12 | 23.5 | 16 | 6.6 | 1874 | 952 | 0.19 | 0.0092992 |  | 1.456 |  | 888 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03006020 | 12 | 23.5 | 20 | 8.6 | 2462 | 1251 | 0.25 | 0.0043691 |  | 1.396 |  | 1144 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03006021 | 12 | 23.5 | 21 | 8.6 | 2457 | 1248 | 0.25 | 0.0062186 |  | 1.468 |  | 1169 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03007010 | 12 | 27.5 | 10 | 4.6 | 1241 | 540 | 0.12 | 0.0013381 |  | 1.403 |  | 578 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03007011 | 12 | 27.5 | 11 | 4.6 | 1665 | 725 | 0.17 | 0.0044311 |  | 1.44 |  | 785 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03007015 | 12 | 27.5 | 15 | 6.6 | 2047 | 891 | 0.2 | 0.003661 |  | 1.396 |  | 951 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03007016 | 12 | 27.5 | 16 | 6.6 | 2186 | 952 | 0.22 | 0.012655 |  | 1.456 |  | 1036 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03007020 | 12 | 27.5 | 20 | 8.6 | 2871 | 1250 | 0.29 | 0.0059704 |  | 1.396 |  | 1334 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03007021 | 12 | 27.5 | 21 | 8.6 | 2867 | 1248 | 0.29 | 0.0085502 |  | 1.468 |  | 1364 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03008010 | 12 | 31.5 | 10 | 4.6 | 1419 | 541 | 0.14 | 0.0019018 |  | 1.403 |  | 661 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03008011 | 12 | 31.5 | 11 | 4.6 | 1903 | 725 | 0.19 | 0.0058317 |  | 1.44 |  | 897 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03008015 | 12 | 31.5 | 15 | 6.6 | 2340 | 892 | 0.23 | 0.0049391 |  | 1.396 |  | 1087 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03008016 | 12 | 31.5 | 16 | 6.6 | 2499 | 952 | 0.25 | 0.016572 |  | 1.456 |  | 1184 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03008020 | 12 | 31.5 | 20 | 8.6 | 3282 | 1250 | 0.33 | 0.0078434 |  | 1.396 |  | 1525 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03008021 | 12 | 31.5 | 21 | 8.6 | 3275 | 1248 | 0.33 | 0.011296 |  | 1.468 |  | 1558 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03009010 | 12 | 35.5 | 10 | 4.6 | 1596 | 541 | 0.16 | 0.0025848 |  | 1.403 |  | 743 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03009011 | 12 | 35.5 | 11 | 4.6 | 2140 | 725 | 0.21 | 0.0074727 |  | 1.44 |  | 1009 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03009015 | 12 | 35.5 | 15 | 6.6 | 2632 | 891 | 0.26 | 0.0064309 |  | 1.396 |  | 1223 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03009016 | 12 | 35.5 | 16 | 6.6 | 2811 | 952 | 0.28 | 0.021066 |  | 1.456 |  | 1332 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03009020 | 12 | 35.5 | 20 | 8.6 | 3691 | 1250 | 0.37 | 0.0099954 |  | 1.396 |  | 1715 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03009021 | 12 | 35.5 | 21 | 8.6 | 3685 | 1248 | 0.37 | 0.014472 |  | 1.468 |  | 1753 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03010010 | 12 | 39.5 | 10 | 4.6 | 1774 | 541 | 0.18 | 0.0033945 |  | 1.403 |  | 826 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03010011 | 12 | 39.5 | 11 | 4.6 | 2378 | 725 | 0.24 | 0.010148 |  | 1.44 |  | 1121 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03010015 | 12 | 39.5 | 15 | 6.6 | 2925 | 892 | 0.29 | 0.0081436 |  | 1.396 |  | 1359 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03010016 | 12 | 39.5 | 16 | 6.6 | 3123 | 952 | 0.31 | 0.026149 |  | 1.456 |  | 1480 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03010020 | 12 | 39.5 | 20 | 8.6 | 4103 | 1251 | 0.41 | 0.012434 |  | 1.396 |  | 1906 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03010021 | 12 | 39.5 | 21 | 8.6 | 4094 | 1248 | 0.41 | 0.01809 |  | 1.468 |  | 1948 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03011010 | 12 | 43.5 | 10 | 4.6 | 1952 | 541 | 0.2 | 0.004338 |  | 1.403 |  | 909 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03011011 | 12 | 43.5 | 11 | 4.6 | 2616 | 725 | 0.26 | 0.012411 |  | 1.44 |  | 1233 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03011015 | 12 | 43.5 | 15 | 6.6 | 3218 | 892 | 0.32 | 0.010084 |  | 1.396 |  | 1495 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03011016 | 12 | 43.5 | 16 | 6.6 | 3435 | 952 | 0.34 | 0.031836 |  | 1.456 |  | 1628 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03011020 | 12 | 43.5 | 20 | 8.6 | 4514 | 1251 | 0.45 | 0.015165 |  | 1.396 |  | 2097 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03011021 | 12 | 43.5 | 21 | 8.6 | 4504 | 1248 | 0.45 | 0.022165 |  | 1.468 |  | 2143 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03012010 | 12 | 47 | 10 | 4.6 | 2128 | 541 | 0.21 | 0.004968 |  | 1.403 |  | 991 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03012011 | 12 | 47 | 11 | 4.6 | 2853 | 725 | 0.29 | 0.015973 |  | 1.44 |  | 1345 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03012015 | 12 | 47 | 15 | 6.6 | 3511 | 892 | 0.35 | 0.012259 |  | 1.396 |  | 1631 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03012016 | 12 | 47 | 16 | 6.6 | 3748 | 952 | 0.37 | 0.038141 |  | 1.456 |  | 1776 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03012020 | 12 | 47 | 20 | 8.6 | 4923 | 1250 | 0.49 | 0.018195 |  | 1.396 |  | 2287 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03012021 | 12 | 47 | 21 | 8.6 | 4914 | 1248 | 0.49 | 0.026711 |  | 1.468 |  | 2338 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03014010 | 12 | 55 | 10 | 4.6 | 2482 | 540 | 0.25 | 0.0074705 |  | 1.403 |  | 1156 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03014011 | 12 | 55 | 11 | 4.6 | 3328 | 725 | 0.33 | 0.022196 |  | 1.44 |  | 1569 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03014015 | 12 | 55 | 15 | 6.6 | 4096 | 892 | 0.41 | 0.017339 |  | 1.396 |  | 1903 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03014016 | 12 | 55 | 16 | 6.6 | 4372 | 952 | 0.44 | 0.05507 |  | 1.456 |  | 2072 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03014020 | 12 | 55 | 20 | 8.6 | 5743 | 1250 | 0.57 | 0.025181 |  | 1.396 |  | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03014021 | 12 | 55 | 21 | 8.6 | 5732 | 1248 | 0.57 | 0.037263 |  | 1.468 |  | 2727 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03016010 | 12 | 63 | 10 | 4.6 | 2839 | 541 | 0.28 | 0.0099346 |  | 1.403 |  | 1322 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03016011 | 12 | 63 | 11 | 4.6 | 3806 | 725 | 0.38 | 0.031233 |  | 1.44 |  | 1794 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03016015 | 12 | 63 | 15 | 6.6 | 4679 | 891 | 0.47 | 0.023435 |  | 1.396 |  | 2174 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03016016 | 12 | 63 | 16 | 6.6 | 4997 | 952 | 0.5 | 0.072587 |  | 1.456 |  | 2368 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03016020 | 12 | 63 | 20 | 8.6 | 6565 | 1251 | 0.66 | 0.034448 |  | 1.396 |  | 3050 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03016021 | 12 | 63 | 21 | 8.6 | 6552 | 1248 | 0.66 | 0.051335 |  | 1.468 |  | 3117 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03018010 | 12 | 71 | 10 | 4.6 | 3193 | 541 | 0.32 | 0.013624 |  | 1.403 |  | 1487 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03018011 | 12 | 71 | 11 | 4.6 | 4281 | 725 | 0.43 | 0.042216 |  | 1.44 |  | 2018 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03018015 | 12 | 71 | 15 | 6.6 | 5265 | 892 | 0.53 | 0.030594 |  | 1.396 |  | 2446 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03018016 | 12 | 71 | 16 | 6.6 | 5622 | 952 | 0.56 | 0.092832 |  | 1.456 |  | 2664 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03018020 | 12 | 71 | 20 | 8.6 | 7385 | 1251 | 0.74 | 0.044172 |  | 1.396 |  | 3431 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03018021 | 12 | 71 | 21 | 8.6 | 7369 | 1248 | 0.74 | 0.066268 |  | 1.468 |  | 3506 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03020010 | 12 | 78.5 | 10 | 4.6 | 3548 | 541 | 0.35 | 0.017121 |  | 1.403 |  | 1652 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03020011 | 12 | 78.5 | 11 | 4.6 | 4756 | 725 | 0.48 | 0.055285 |  | 1.44 |  | 2242 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03020015 | 12 | 78.5 | 15 | 6.6 | 5850 | 892 | 0.59 | 0.038864 |  | 1.396 |  | 2718 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03020016 | 12 | 78.5 | 16 | 6.6 | 6246 | 952 | 0.62 | 0.1159 |  | 1.456 |  | 2960 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03020020 | 12 | 78.5 | 20 | 8.6 | 8205 | 1250 | 0.82 | 0.055268 |  | 1.396 |  | 3812 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03020021 | 12 | 78.5 | 21 | 8.6 | 8189 | 1248 | 0.82 | 0.083428 |  | 1.468 |  | 3896 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03022010 | 12 | 86.5 | 10 | 4.6 | 3902 | 541 | 0.39 | 0.022162 |  | 1.403 |  | 1817 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03022011 | 12 | 86.5 | 11 | 4.6 | 5231 | 725 | 0.52 | 0.068152 |  | 1.44 |  | 2466 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03022015 | 12 | 86.5 | 15 | 6.6 | 6436 | 892 | 0.64 | 0.04688 |  | 1.396 |  | 2990 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03022016 | 12 | 86.5 | 16 | 6.6 | 6871 | 952 | 0.69 | 0.14594 |  | 1.456 |  | 3256 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03022020 | 12 | 86.5 | 20 | 8.6 | 9025 | 1250 | 0.9 | 0.06778 |  | 1.396 |  | 4193 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03022021 | 12 | 86.5 | 21 | 8.6 | 9009 | 1248 | 0.9 | 0.1029 |  | 1.468 |  | 4286 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03024010 | 12 | 94.5 | 10 | 4.6 | 4256 | 541 | 0.43 | 0.028012 |  | 1.403 |  | 1982 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03024011 | 12 | 94.5 | 11 | 4.6 | 5707 | 725 | 0.57 | 0.085461 |  | 1.44 |  | 2690 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03024015 | 12 | 94.5 | 15 | 6.6 | 7021 | 892 | 0.7 | 0.057344 |  | 1.396 |  | 3262 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03024016 | 12 | 94.5 | 16 | 6.6 | 7496 | 952 | 0.75 | 0.17534 |  | 1.456 |  | 3552 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03024020 | 12 | 94.5 | 20 | 8.6 | 9845 | 1250 | 0.98 | 0.081751 |  | 1.396 |  | 4574 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03024021 | 12 | 94.5 | 21 | 8.6 | 9826 | 1248 | 0.98 | 0.12478 |  | 1.468 |  | 4675 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03026010 | 12 | 102.5 | 10 | 4.6 | 4613 | 541 | 0.46 | 0.033371 |  | 1.403 |  | 2148 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03026011 | 12 | 102.5 | 11 | 4.6 | 6184 | 725 | 0.62 | 0.10524 |  | 1.44 |  | 2915 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03026015 | 12 | 102.5 | 15 | 6.6 | 7605 | 892 | 0.76 | 0.069047 |  | 1.396 |  | 3533 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03026016 | 12 | 102.5 | 16 | 6.6 | 8120 | 952 | 0.81 | 0.20783 |  | 1.456 |  | 3848 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03026020 | 12 | 102.5 | 20 | 8.6 | 10667 | 1251 | 1.07 | 0.098998 |  | 1.396 |  | 4956 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03026021 | 12 | 102.5 | 21 | 8.6 | 10646 | 1248 | 1.06 | 0.14915 |  | 1.468 |  | 5065 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03028010 | 12 | 110 | 10 | 4.6 | 4967 | 541 | 0.5 | 0.04081 |  | 1.403 |  | 2313 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03028011 | 12 | 110 | 11 | 4.6 | 6659 | 725 | 0.67 | 0.12762 |  | 1.44 |  | 3139 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03028015 | 12 | 110 | 15 | 6.6 | 8190 | 892 | 0.82 | 0.082031 |  | 1.396 |  | 3805 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03028016 | 12 | 110 | 16 | 6.6 | 8745 | 952 | 0.87 | 0.24349 |  | 1.456 |  | 4144 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03028020 | 12 | 110 | 20 | 8.6 | 11487 | 1250 | 1.15 | 0.11617 |  | 1.396 |  | 5337 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03028021 | 12 | 110 | 21 | 8.6 | 11464 | 1248 | 1.15 | 0.17903 |  | 1.468 |  | 5454 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.03030010 | 12 | 118 | 10 | 4.6 | 5321 | 541 | 0.53 | 0.047527 |  | 1.403 |  | 2478 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.03030011 | 12 | 118 | 11 | 4.6 | 7134 | 725 | 0.71 | 0.14887 |  | 1.44 |  | 3363 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.03030015 | 12 | 118 | 15 | 6.6 | 8775 | 892 | 0.88 | 0.096338 |  | 1.396 |  | 4077 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.03030016 | 12 | 118 | 16 | 6.6 | 9369 | 952 | 0.94 | 0.28828 |  | 1.456 |  | 4440 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.03030020 | 12 | 118 | 20 | 8.6 | 12308 | 1250 | 1.23 | 0.13494 |  | 1.396 |  | 5718 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.03030021 | 12 | 118 | 21 | 8.6 | 12283 | 1248 | 1.23 | 0.20888 |  | 1.468 |  | 5844 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04004010 | 15.5 | 15.5 | 10 | 4.6 | 829 | 632 | 0.08 | 0.00049816 |  | 1.394 |  | 385 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04004011 | 15.5 | 15.5 | 11 | 4.6 | 1074 | 818 | 0.11 | 0.0015251 |  | 1.439 |  | 506 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04004015 | 15.5 | 15.5 | 15 | 6.6 | 1354 | 1032 | 0.14 | 0.0016625 |  | 1.385 |  | 627 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04004016 | 15.5 | 15.5 | 16 | 6.6 | 1433 | 1092 | 0.14 | 0.0048759 |  | 1.46 |  | 680 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04004020 | 15.5 | 15.5 | 20 | 8.6 | 1897 | 1446 | 0.19 | 0.0024328 |  | 1.384 |  | 878 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04004021 | 15.5 | 15.5 | 21 | 8.6 | 1907 | 1453 | 0.19 | 0.0034102 |  | 1.477 |  | 910 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04005010 | 15.5 | 19.5 | 10 | 4.6 | 1038 | 633 | 0.1 | 0.00082769 |  | 1.394 |  | 482 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04005011 | 15.5 | 19.5 | 11 | 4.6 | 1341 | 817 | 0.13 | 0.0022931 |  | 1.439 |  | 632 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04005015 | 15.5 | 19.5 | 15 | 6.6 | 1694 | 1033 | 0.17 | 0.002515 |  | 1.385 |  | 784 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04005016 | 15.5 | 19.5 | 16 | 6.6 | 1791 | 1092 | 0.18 | 0.0081936 |  | 1.46 |  | 850 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04005020 | 15.5 | 19.5 | 20 | 8.6 | 2373 | 1447 | 0.24 | 0.0039492 |  | 1.384 |  | 1098 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04005021 | 15.5 | 19.5 | 21 | 8.6 | 2383 | 1453 | 0.24 | 0.0055763 |  | 1.477 |  | 1137 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04006010 | 15.5 | 23.5 | 10 | 4.6 | 1245 | 632 | 0.12 | 0.0012579 |  | 1.394 |  | 578 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04006011 | 15.5 | 23.5 | 11 | 4.6 | 1609 | 817 | 0.16 | 0.0036844 |  | 1.439 |  | 758 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04006015 | 15.5 | 23.5 | 15 | 6.6 | 2033 | 1033 | 0.2 | 0.0035629 |  | 1.385 |  | 941 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04006016 | 15.5 | 23.5 | 16 | 6.6 | 2150 | 1092 | 0.22 | 0.012424 |  | 1.46 |  | 1020 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04006020 | 15.5 | 23.5 | 20 | 8.6 | 2848 | 1447 | 0.28 | 0.0054651 |  | 1.384 |  | 1318 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04006021 | 15.5 | 23.5 | 21 | 8.6 | 2858 | 1452 | 0.29 | 0.0083243 |  | 1.477 |  | 1364 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04007010 | 15.5 | 27.5 | 10 | 4.6 | 1452 | 632 | 0.15 | 0.0020507 |  | 1.394 |  | 674 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04007011 | 15.5 | 27.5 | 11 | 4.6 | 1878 | 818 | 0.19 | 0.0054758 |  | 1.439 |  | 885 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04007015 | 15.5 | 27.5 | 15 | 6.6 | 2372 | 1033 | 0.24 | 0.0052333 |  | 1.385 |  | 1098 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04007016 | 15.5 | 27.5 | 16 | 6.6 | 2508 | 1092 | 0.25 | 0.016284 |  | 1.46 |  | 1190 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04007020 | 15.5 | 27.5 | 20 | 8.6 | 3321 | 1446 | 0.33 | 0.0077023 |  | 1.384 |  | 1537 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04007021 | 15.5 | 27.5 | 21 | 8.6 | 3336 | 1453 | 0.33 | 0.011014 |  | 1.477 |  | 1592 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04008010 | 15.5 | 31.5 | 10 | 4.6 | 1658 | 632 | 0.17 | 0.0027532 |  | 1.394 |  | 770 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04008011 | 15.5 | 31.5 | 11 | 4.6 | 2145 | 817 | 0.21 | 0.0070493 |  | 1.439 |  | 1011 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04008015 | 15.5 | 31.5 | 15 | 6.6 | 2709 | 1032 | 0.27 | 0.0067576 |  | 1.385 |  | 1254 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04008016 | 15.5 | 31.5 | 16 | 6.6 | 2866 | 1092 | 0.29 | 0.022198 |  | 1.46 |  | 1360 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04008020 | 15.5 | 31.5 | 20 | 8.6 | 3797 | 1447 | 0.38 | 0.010353 |  | 1.384 |  | 1757 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04008021 | 15.5 | 31.5 | 21 | 8.6 | 3812 | 1452 | 0.38 | 0.014884 |  | 1.477 |  | 1819 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04009010 | 15.5 | 35.5 | 10 | 4.6 | 1867 | 632 | 0.19 | 0.0035822 |  | 1.394 |  | 867 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04009011 | 15.5 | 35.5 | 11 | 4.6 | 2415 | 818 | 0.24 | 0.0096146 |  | 1.439 |  | 1138 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04009015 | 15.5 | 35.5 | 15 | 6.6 | 3048 | 1032 | 0.3 | 0.0085018 |  | 1.385 |  | 1411 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04009016 | 15.5 | 35.5 | 16 | 6.6 | 3224 | 1092 | 0.32 | 0.027389 |  | 1.46 |  | 1530 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04009020 | 15.5 | 35.5 | 20 | 8.6 | 4270 | 1446 | 0.43 | 0.013428 |  | 1.384 |  | 1976 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04009021 | 15.5 | 35.5 | 21 | 8.6 | 4290 | 1453 | 0.43 | 0.019402 |  | 1.477 |  | 2047 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04010010 | 15.5 | 39.5 | 10 | 4.6 | 2074 | 632 | 0.21 | 0.0045446 |  | 1.394 |  | 963 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04010011 | 15.5 | 39.5 | 11 | 4.6 | 2682 | 817 | 0.27 | 0.012666 |  | 1.439 |  | 1264 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04010015 | 15.5 | 39.5 | 15 | 6.6 | 3387 | 1032 | 0.34 | 0.0111 |  | 1.385 |  | 1568 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04010016 | 15.5 | 39.5 | 16 | 6.6 | 3583 | 1092 | 0.36 | 0.03507 |  | 1.46 |  | 1700 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04010020 | 15.5 | 39.5 | 20 | 8.6 | 4745 | 1446 | 0.47 | 0.016253 |  | 1.384 |  | 2196 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04010021 | 15.5 | 39.5 | 21 | 8.6 | 4765 | 1452 | 0.48 | 0.024588 |  | 1.477 |  | 2274 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04011010 | 15.5 | 43.5 | 10 | 4.6 | 2281 | 632 | 0.23 | 0.0056475 |  | 1.394 |  | 1059 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04011011 | 15.5 | 43.5 | 11 | 4.6 | 2950 | 817 | 0.3 | 0.016232 |  | 1.439 |  | 1390 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04011015 | 15.5 | 43.5 | 15 | 6.6 | 3726 | 1032 | 0.37 | 0.013371 |  | 1.385 |  | 1725 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04011016 | 15.5 | 43.5 | 16 | 6.6 | 3941 | 1092 | 0.39 | 0.04166 |  | 1.46 |  | 1870 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04011020 | 15.5 | 43.5 | 20 | 8.6 | 5221 | 1447 | 0.52 | 0.020128 |  | 1.384 |  | 2416 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04011021 | 15.5 | 43.5 | 21 | 8.6 | 5241 | 1452 | 0.52 | 0.029356 |  | 1.477 |  | 2501 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04012010 | 15.5 | 47 | 10 | 4.6 | 2490 | 632 | 0.25 | 0.0068976 |  | 1.394 |  | 1156 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04012011 | 15.5 | 47 | 11 | 4.6 | 3219 | 818 | 0.32 | 0.019203 |  | 1.439 |  | 1517 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04012015 | 15.5 | 47 | 15 | 6.6 | 4066 | 1033 | 0.41 | 0.016663 |  | 1.385 |  | 1882 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04012016 | 15.5 | 47 | 16 | 6.6 | 4299 | 1092 | 0.43 | 0.051186 |  | 1.46 |  | 2040 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04012020 | 15.5 | 47 | 20 | 8.6 | 5694 | 1446 | 0.57 | 0.024458 |  | 1.384 |  | 2635 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04012021 | 15.5 | 47 | 21 | 8.6 | 5719 | 1453 | 0.57 | 0.035817 |  | 1.477 |  | 2729 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04014010 | 15.5 | 55 | 10 | 4.6 | 2903 | 632 | 0.29 | 0.0098653 |  | 1.394 |  | 1348 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04014011 | 15.5 | 55 | 11 | 4.6 | 3756 | 818 | 0.38 | 0.028864 |  | 1.439 |  | 1770 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04014015 | 15.5 | 55 | 15 | 6.6 | 4742 | 1032 | 0.47 | 0.022579 |  | 1.385 |  | 2195 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04014016 | 15.5 | 55 | 16 | 6.6 | 5016 | 1092 | 0.5 | 0.070684 |  | 1.46 |  | 2380 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04014020 | 15.5 | 55 | 20 | 8.6 | 6643 | 1446 | 0.66 | 0.033517 |  | 1.384 |  | 3074 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04014021 | 15.5 | 55 | 21 | 8.6 | 6673 | 1453 | 0.67 | 0.050933 |  | 1.477 |  | 3184 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04016010 | 15.5 | 63 | 10 | 4.6 | 3319 | 632 | 0.33 | 0.013499 |  | 1.394 |  | 1541 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04016011 | 15.5 | 63 | 11 | 4.6 | 4291 | 817 | 0.43 | 0.03928 |  | 1.439 |  | 2022 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04016015 | 15.5 | 63 | 15 | 6.6 | 5420 | 1033 | 0.54 | 0.030626 |  | 1.385 |  | 2509 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04016016 | 15.5 | 63 | 16 | 6.6 | 5732 | 1092 | 0.57 | 0.093695 |  | 1.46 |  | 2720 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04016020 | 15.5 | 63 | 20 | 8.6 | 7594 | 1447 | 0.76 | 0.045332 |  | 1.384 |  | 3514 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04016021 | 15.5 | 63 | 21 | 8.6 | 7624 | 1452 | 0.76 | 0.067378 |  | 1.477 |  | 3638 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04018010 | 15.5 | 71 | 10 | 4.6 | 3733 | 632 | 0.37 | 0.017846 |  | 1.394 |  | 1733 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04018011 | 15.5 | 71 | 11 | 4.6 | 4828 | 818 | 0.48 | 0.051733 |  | 1.439 |  | 2275 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04018015 | 15.5 | 71 | 15 | 6.6 | 6096 | 1032 | 0.61 | 0.040087 |  | 1.385 |  | 2822 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04018016 | 15.5 | 71 | 16 | 6.6 | 6449 | 1092 | 0.64 | 0.12034 |  | 1.46 |  | 3060 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04018020 | 15.5 | 71 | 20 | 8.6 | 8542 | 1446 | 0.85 | 0.057812 |  | 1.384 |  | 3953 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04018021 | 15.5 | 71 | 21 | 8.6 | 8577 | 1452 | 0.86 | 0.088465 |  | 1.477 |  | 4093 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04020010 | 15.5 | 78.5 | 10 | 4.6 | 4148 | 632 | 0.41 | 0.022956 |  | 1.394 |  | 1926 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04020011 | 15.5 | 78.5 | 11 | 4.6 | 5365 | 818 | 0.54 | 0.068687 |  | 1.439 |  | 2528 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04020015 | 15.5 | 78.5 | 15 | 6.6 | 6775 | 1033 | 0.68 | 0.051025 |  | 1.385 |  | 3136 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04020016 | 15.5 | 78.5 | 16 | 6.6 | 7165 | 1092 | 0.72 | 0.1549 |  | 1.46 |  | 3400 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04020020 | 15.5 | 78.5 | 20 | 8.6 | 9491 | 1446 | 0.95 | 0.073505 |  | 1.384 |  | 4392 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04020021 | 15.5 | 78.5 | 21 | 8.6 | 9531 | 1453 | 0.95 | 0.11063 |  | 1.477 |  | 4548 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04022010 | 15.5 | 86.5 | 10 | 4.6 | 4564 | 632 | 0.46 | 0.030071 |  | 1.394 |  | 2119 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04022011 | 15.5 | 86.5 | 11 | 4.6 | 5902 | 818 | 0.59 | 0.085955 |  | 1.439 |  | 2781 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04022015 | 15.5 | 86.5 | 15 | 6.6 | 7453 | 1033 | 0.75 | 0.063499 |  | 1.385 |  | 3450 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04022016 | 15.5 | 86.5 | 16 | 6.6 | 7882 | 1092 | 0.79 | 0.18967 |  | 1.46 |  | 3740 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04022020 | 15.5 | 86.5 | 20 | 8.6 | 10440 | 1446 | 1.04 | 0.089647 |  | 1.384 |  | 4831 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04022021 | 15.5 | 86.5 | 21 | 8.6 | 10485 | 1453 | 1.05 | 0.1382 |  | 1.477 |  | 5003 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04024010 | 15.5 | 94.5 | 10 | 4.6 | 4978 | 632 | 0.5 | 0.036997 |  | 1.394 |  | 2311 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04024011 | 15.5 | 94.5 | 11 | 4.6 | 6438 | 818 | 0.64 | 0.10568 |  | 1.439 |  | 3034 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04024015 | 15.5 | 94.5 | 15 | 6.6 | 8129 | 1032 | 0.81 | 0.075768 |  | 1.385 |  | 3763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04024016 | 15.5 | 94.5 | 16 | 6.6 | 8598 | 1092 | 0.86 | 0.22844 |  | 1.46 |  | 4080 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04024020 | 15.5 | 94.5 | 20 | 8.6 | 11388 | 1446 | 1.14 | 0.10947 |  | 1.384 |  | 5270 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04024021 | 15.5 | 94.5 | 21 | 8.6 | 11438 | 1453 | 1.14 | 0.16654 |  | 1.477 |  | 5458 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04026010 | 15.5 | 102.5 | 10 | 4.6 | 5393 | 632 | 0.54 | 0.044825 |  | 1.394 |  | 2504 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04026011 | 15.5 | 102.5 | 11 | 4.6 | 6973 | 817 | 0.7 | 0.1314 |  | 1.439 |  | 3286 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04026015 | 15.5 | 102.5 | 15 | 6.6 | 8807 | 1032 | 0.88 | 0.091294 |  | 1.385 |  | 4077 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04026016 | 15.5 | 102.5 | 16 | 6.6 | 9315 | 1092 | 0.93 | 0.27132 |  | 1.46 |  | 4420 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04026020 | 15.5 | 102.5 | 20 | 8.6 | 12339 | 1447 | 1.23 | 0.1295 |  | 1.384 |  | 5710 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04026021 | 15.5 | 102.5 | 21 | 8.6 | 12389 | 1452 | 1.24 | 0.20108 |  | 1.477 |  | 5912 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04028010 | 15.5 | 110 | 10 | 4.6 | 5807 | 632 | 0.58 | 0.053598 |  | 1.394 |  | 2696 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04028011 | 15.5 | 110 | 11 | 4.6 | 7510 | 818 | 0.75 | 0.1568 |  | 1.439 |  | 3539 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04028015 | 15.5 | 110 | 15 | 6.6 | 9484 | 1032 | 0.95 | 0.10852 |  | 1.385 |  | 4390 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04028016 | 15.5 | 110 | 16 | 6.6 | 10031 | 1092 | 1 | 0.31842 |  | 1.46 |  | 4760 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04028020 | 15.5 | 110 | 20 | 8.6 | 13288 | 1446 | 1.33 | 0.15368 |  | 1.384 |  | 6149 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04028021 | 15.5 | 110 | 21 | 8.6 | 13343 | 1452 | 1.33 | 0.23605 |  | 1.477 |  | 6367 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.04030010 | 15.5 | 118 | 10 | 4.6 | 6222 | 632 | 0.62 | 0.063358 |  | 1.394 |  | 2889 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.04030011 | 15.5 | 118 | 11 | 4.6 | 8047 | 818 | 0.8 | 0.18505 |  | 1.439 |  | 3792 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.04030015 | 15.5 | 118 | 15 | 6.6 | 10162 | 1032 | 1.02 | 0.1275 |  | 1.385 |  | 4704 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.04030016 | 15.5 | 118 | 16 | 6.6 | 10748 | 1092 | 1.07 | 0.36986 |  | 1.46 |  | 5100 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.04030020 | 15.5 | 118 | 20 | 8.6 | 14236 | 1446 | 1.42 | 0.17782 |  | 1.384 |  | 6588 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.04030021 | 15.5 | 118 | 21 | 8.6 | 14296 | 1452 | 1.43 | 0.27803 |  | 1.477 |  | 6822 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05004010 | 19.5 | 15.5 | 10 | 4.6 | 929 | 708 | 0.09 | 0.00062652 |  | 1.385 |  | 430 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05004011 | 19.5 | 15.5 | 11 | 4.6 | 1176 | 896 | 0.12 | 0.0018055 |  | 1.438 |  | 554 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05004015 | 19.5 | 15.5 | 15 | 6.6 | 1505 | 1147 | 0.15 | 0.0019055 |  | 1.373 |  | 694 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05004016 | 19.5 | 15.5 | 16 | 6.6 | 1597 | 1217 | 0.16 | 0.0063557 |  | 1.464 |  | 759 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05004020 | 19.5 | 15.5 | 20 | 8.6 | 2104 | 1603 | 0.21 | 0.0029673 |  | 1.373 |  | 970 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05004021 | 19.5 | 15.5 | 21 | 8.6 | 2159 | 1645 | 0.22 | 0.0045572 |  | 1.485 |  | 1033 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05005010 | 19.5 | 19.5 | 10 | 4.6 | 1162 | 708 | 0.12 | 0.0011777 |  | 1.385 |  | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05005011 | 19.5 | 19.5 | 11 | 4.6 | 1471 | 897 | 0.15 | 0.0030203 |  | 1.438 |  | 693 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05005015 | 19.5 | 19.5 | 15 | 6.6 | 1880 | 1146 | 0.19 | 0.0031316 |  | 1.373 |  | 867 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05005016 | 19.5 | 19.5 | 16 | 6.6 | 1997 | 1217 | 0.2 | 0.010095 |  | 1.464 |  | 949 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05005020 | 19.5 | 19.5 | 20 | 8.6 | 2631 | 1604 | 0.26 | 0.0046274 |  | 1.373 |  | 1213 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05005021 | 19.5 | 19.5 | 21 | 8.6 | 2698 | 1645 | 0.27 | 0.0070338 |  | 1.485 |  | 1291 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05006010 | 19.5 | 23.5 | 10 | 4.6 | 1396 | 709 | 0.14 | 0.0016922 |  | 1.385 |  | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05006011 | 19.5 | 23.5 | 11 | 4.6 | 1766 | 897 | 0.18 | 0.0046161 |  | 1.438 |  | 832 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05006015 | 19.5 | 23.5 | 15 | 6.6 | 2256 | 1146 | 0.23 | 0.0046896 |  | 1.373 |  | 1040 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05006016 | 19.5 | 23.5 | 16 | 6.6 | 2397 | 1218 | 0.24 | 0.014756 |  | 1.464 |  | 1139 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05006020 | 19.5 | 23.5 | 20 | 8.6 | 3156 | 1603 | 0.32 | 0.007115 |  | 1.373 |  | 1455 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05006021 | 19.5 | 23.5 | 21 | 8.6 | 3238 | 1645 | 0.32 | 0.010102 |  | 1.485 |  | 1549 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05007010 | 19.5 | 27.5 | 10 | 4.6 | 1627 | 708 | 0.16 | 0.0023206 |  | 1.385 |  | 753 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05007011 | 19.5 | 27.5 | 11 | 4.6 | 2059 | 897 | 0.21 | 0.0066259 |  | 1.438 |  | 970 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05007015 | 19.5 | 27.5 | 15 | 6.6 | 2633 | 1146 | 0.26 | 0.0061227 |  | 1.373 |  | 1214 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05007016 | 19.5 | 27.5 | 16 | 6.6 | 2797 | 1218 | 0.28 | 0.020365 |  | 1.464 |  | 1329 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05007020 | 19.5 | 27.5 | 20 | 8.6 | 3683 | 1604 | 0.37 | 0.0096517 |  | 1.373 |  | 1698 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05007021 | 19.5 | 27.5 | 21 | 8.6 | 3777 | 1645 | 0.38 | 0.014525 |  | 1.485 |  | 1807 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05008010 | 19.5 | 31.5 | 10 | 4.6 | 1860 | 709 | 0.19 | 0.0034042 |  | 1.385 |  | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05008011 | 19.5 | 31.5 | 11 | 4.6 | 2354 | 897 | 0.24 | 0.0090809 |  | 1.438 |  | 1109 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05008015 | 19.5 | 31.5 | 15 | 6.6 | 3008 | 1146 | 0.3 | 0.0083046 |  | 1.373 |  | 1387 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05008016 | 19.5 | 31.5 | 16 | 6.6 | 3195 | 1217 | 0.32 | 0.026948 |  | 1.464 |  | 1518 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05008020 | 19.5 | 31.5 | 20 | 8.6 | 4208 | 1603 | 0.42 | 0.012608 |  | 1.373 |  | 1940 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05008021 | 19.5 | 31.5 | 21 | 8.6 | 4318 | 1645 | 0.43 | 0.018957 |  | 1.485 |  | 2066 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05009010 | 19.5 | 35.5 | 10 | 4.6 | 2091 | 708 | 0.21 | 0.0043329 |  | 1.385 |  | 968 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05009011 | 19.5 | 35.5 | 11 | 4.6 | 2647 | 896 | 0.26 | 0.011184 |  | 1.438 |  | 1247 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05009015 | 19.5 | 35.5 | 15 | 6.6 | 3386 | 1147 | 0.34 | 0.010855 |  | 1.373 |  | 1561 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05009016 | 19.5 | 35.5 | 16 | 6.6 | 3595 | 1218 | 0.36 | 0.03453 |  | 1.464 |  | 1708 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05009020 | 19.5 | 35.5 | 20 | 8.6 | 4735 | 1604 | 0.47 | 0.015994 |  | 1.373 |  | 2183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05009021 | 19.5 | 35.5 | 21 | 8.6 | 4857 | 1645 | 0.49 | 0.025038 |  | 1.485 |  | 2324 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05010010 | 19.5 | 39.5 | 10 | 4.6 | 2324 | 708 | 0.23 | 0.0053996 |  | 1.385 |  | 1076 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05010011 | 19.5 | 39.5 | 11 | 4.6 | 2942 | 897 | 0.29 | 0.014491 |  | 1.438 |  | 1386 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05010015 | 19.5 | 39.5 | 15 | 6.6 | 3761 | 1146 | 0.38 | 0.013786 |  | 1.373 |  | 1734 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05010016 | 19.5 | 39.5 | 16 | 6.6 | 3995 | 1218 | 0.4 | 0.043132 |  | 1.464 |  | 1898 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05010020 | 19.5 | 39.5 | 20 | 8.6 | 5259 | 1603 | 0.53 | 0.020575 |  | 1.373 |  | 2425 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05010021 | 19.5 | 39.5 | 21 | 8.6 | 5397 | 1645 | 0.54 | 0.030932 |  | 1.485 |  | 2582 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05011010 | 19.5 | 43.5 | 10 | 4.6 | 2558 | 709 | 0.26 | 0.0071199 |  | 1.385 |  | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05011011 | 19.5 | 43.5 | 11 | 4.6 | 3237 | 897 | 0.32 | 0.018324 |  | 1.438 |  | 1525 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05011015 | 19.5 | 43.5 | 15 | 6.6 | 4136 | 1146 | 0.41 | 0.016325 |  | 1.373 |  | 1907 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05011016 | 19.5 | 43.5 | 16 | 6.6 | 4395 | 1218 | 0.44 | 0.05278 |  | 1.464 |  | 2088 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05011020 | 19.5 | 43.5 | 20 | 8.6 | 5786 | 1603 | 0.58 | 0.024932 |  | 1.373 |  | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05011021 | 19.5 | 43.5 | 21 | 8.6 | 5936 | 1645 | 0.59 | 0.037529 |  | 1.485 |  | 2840 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05012010 | 19.5 | 47 | 10 | 4.6 | 2789 | 708 | 0.28 | 0.0085399 |  | 1.385 |  | 1291 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05012011 | 19.5 | 47 | 11 | 4.6 | 3530 | 897 | 0.35 | 0.022711 |  | 1.438 |  | 1663 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05012015 | 19.5 | 47 | 15 | 6.6 | 4513 | 1146 | 0.45 | 0.019964 |  | 1.373 |  | 2081 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05012016 | 19.5 | 47 | 16 | 6.6 | 4794 | 1218 | 0.48 | 0.063493 |  | 1.464 |  | 2278 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05012020 | 19.5 | 47 | 20 | 8.6 | 6311 | 1603 | 0.63 | 0.02975 |  | 1.373 |  | 2910 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05012021 | 19.5 | 47 | 21 | 8.6 | 6475 | 1645 | 0.65 | 0.04622 |  | 1.485 |  | 3098 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05014010 | 19.5 | 55 | 10 | 4.6 | 3253 | 708 | 0.33 | 0.012571 |  | 1.385 |  | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05014011 | 19.5 | 55 | 11 | 4.6 | 4118 | 897 | 0.41 | 0.033256 |  | 1.438 |  | 1940 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05014015 | 19.5 | 55 | 15 | 6.6 | 5266 | 1146 | 0.53 | 0.028489 |  | 1.373 |  | 2428 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05014016 | 19.5 | 55 | 16 | 6.6 | 5592 | 1217 | 0.56 | 0.088204 |  | 1.464 |  | 2657 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05014020 | 19.5 | 55 | 20 | 8.6 | 7363 | 1603 | 0.74 | 0.041905 |  | 1.373 |  | 3395 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05014021 | 19.5 | 55 | 21 | 8.6 | 7556 | 1645 | 0.76 | 0.065004 |  | 1.485 |  | 3615 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05016010 | 19.5 | 63 | 10 | 4.6 | 3720 | 709 | 0.37 | 0.016715 |  | 1.385 |  | 1722 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05016011 | 19.5 | 63 | 11 | 4.6 | 4708 | 897 | 0.47 | 0.046333 |  | 1.438 |  | 2218 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05016015 | 19.5 | 63 | 15 | 6.6 | 6016 | 1146 | 0.6 | 0.03753 |  | 1.373 |  | 2774 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05016016 | 19.5 | 63 | 16 | 6.6 | 6392 | 1218 | 0.64 | 0.11743 |  | 1.464 |  | 3037 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05016020 | 19.5 | 63 | 20 | 8.6 | 8415 | 1603 | 0.84 | 0.055088 |  | 1.373 |  | 3880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05016021 | 19.5 | 63 | 21 | 8.6 | 8634 | 1645 | 0.86 | 0.085528 |  | 1.485 |  | 4131 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05018010 | 19.5 | 71 | 10 | 4.6 | 4184 | 708 | 0.42 | 0.022597 |  | 1.385 |  | 1937 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05018011 | 19.5 | 71 | 11 | 4.6 | 5296 | 897 | 0.53 | 0.062141 |  | 1.438 |  | 2495 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05018015 | 19.5 | 71 | 15 | 6.6 | 6769 | 1146 | 0.68 | 0.049408 |  | 1.373 |  | 3121 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05018016 | 19.5 | 71 | 16 | 6.6 | 7190 | 1218 | 0.72 | 0.15133 |  | 1.464 |  | 3416 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05018020 | 19.5 | 71 | 20 | 8.6 | 9467 | 1603 | 0.95 | 0.071762 |  | 1.373 |  | 4365 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05018021 | 19.5 | 71 | 21 | 8.6 | 9715 | 1645 | 0.97 | 0.11152 |  | 1.485 |  | 4648 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05020010 | 19.5 | 78.5 | 10 | 4.6 | 4649 | 709 | 0.46 | 0.028422 |  | 1.385 |  | 2152 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05020011 | 19.5 | 78.5 | 11 | 4.6 | 5884 | 897 | 0.59 | 0.080874 |  | 1.438 |  | 2772 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05020015 | 19.5 | 78.5 | 15 | 6.6 | 7521 | 1146 | 0.75 | 0.061584 |  | 1.373 |  | 3468 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05020016 | 19.5 | 78.5 | 16 | 6.6 | 7989 | 1218 | 0.8 | 0.19007 |  | 1.464 |  | 3796 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05020020 | 19.5 | 78.5 | 20 | 8.6 | 10519 | 1603 | 1.05 | 0.089252 |  | 1.373 |  | 4850 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05020021 | 19.5 | 78.5 | 21 | 8.6 | 10793 | 1645 | 1.08 | 0.14151 |  | 1.485 |  | 5164 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05022010 | 19.5 | 86.5 | 10 | 4.6 | 5113 | 708 | 0.51 | 0.036401 |  | 1.385 |  | 2367 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05022011 | 19.5 | 86.5 | 11 | 4.6 | 6472 | 897 | 0.65 | 0.10272 |  | 1.438 |  | 3049 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05022015 | 19.5 | 86.5 | 15 | 6.6 | 8274 | 1146 | 0.83 | 0.077102 |  | 1.373 |  | 3815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05022016 | 19.5 | 86.5 | 16 | 6.6 | 8789 | 1218 | 0.88 | 0.23378 |  | 1.464 |  | 4176 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05022020 | 19.5 | 86.5 | 20 | 8.6 | 11571 | 1603 | 1.16 | 0.11075 |  | 1.373 |  | 5335 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05022021 | 19.5 | 86.5 | 21 | 8.6 | 11872 | 1645 | 1.19 | 0.17564 |  | 1.485 |  | 5680 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05024010 | 19.5 | 94.5 | 10 | 4.6 | 5578 | 708 | 0.56 | 0.045609 |  | 1.385 |  | 2582 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05024011 | 19.5 | 94.5 | 11 | 4.6 | 7060 | 897 | 0.71 | 0.12785 |  | 1.438 |  | 3326 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05024015 | 19.5 | 94.5 | 15 | 6.6 | 9027 | 1146 | 0.9 | 0.092669 |  | 1.373 |  | 4162 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05024016 | 19.5 | 94.5 | 16 | 6.6 | 9587 | 1218 | 0.96 | 0.28261 |  | 1.464 |  | 4555 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05024020 | 19.5 | 94.5 | 20 | 8.6 | 12623 | 1603 | 1.26 | 0.13282 |  | 1.373 |  | 5820 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05024021 | 19.5 | 94.5 | 21 | 8.6 | 12952 | 1645 | 1.3 | 0.21406 |  | 1.485 |  | 6197 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05026010 | 19.5 | 102.5 | 10 | 4.6 | 6044 | 709 | 0.6 | 0.054428 |  | 1.385 |  | 2798 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05026011 | 19.5 | 102.5 | 11 | 4.6 | 7651 | 897 | 0.77 | 0.15646 |  | 1.438 |  | 3604 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05026015 | 19.5 | 102.5 | 15 | 6.6 | 9777 | 1146 | 0.98 | 0.1121 |  | 1.373 |  | 4508 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05026016 | 19.5 | 102.5 | 16 | 6.6 | 10386 | 1218 | 1.04 | 0.33671 |  | 1.464 |  | 4935 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05026020 | 19.5 | 102.5 | 20 | 8.6 | 13674 | 1603 | 1.37 | 0.15943 |  | 1.373 |  | 6305 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05026021 | 19.5 | 102.5 | 21 | 8.6 | 14031 | 1645 | 1.4 | 0.25346 |  | 1.485 |  | 6713 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05028010 | 19.5 | 110 | 10 | 4.6 | 6509 | 709 | 0.65 | 0.066091 |  | 1.385 |  | 3013 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05028011 | 19.5 | 110 | 11 | 4.6 | 8239 | 897 | 0.82 | 0.18457 |  | 1.438 |  | 3881 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05028015 | 19.5 | 110 | 15 | 6.6 | 10530 | 1146 | 1.05 | 0.1313 |  | 1.373 |  | 4855 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05028016 | 19.5 | 110 | 16 | 6.6 | 11184 | 1217 | 1.12 | 0.39621 |  | 1.464 |  | 5314 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05028020 | 19.5 | 110 | 20 | 8.6 | 14726 | 1603 | 1.47 | 0.18636 |  | 1.373 |  | 6790 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05028021 | 19.5 | 110 | 21 | 8.6 | 15112 | 1645 | 1.51 | 0.30058 |  | 1.485 |  | 7230 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.05030010 | 19.5 | 118 | 10 | 4.6 | 6973 | 708 | 0.7 | 0.079166 |  | 1.385 |  | 3228 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.05030011 | 19.5 | 118 | 11 | 4.6 | 8827 | 897 | 0.88 | 0.22019 |  | 1.438 |  | 4158 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.05030015 | 19.5 | 118 | 15 | 6.6 | 11282 | 1146 | 1.13 | 0.15489 |  | 1.373 |  | 5202 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.05030016 | 19.5 | 118 | 16 | 6.6 | 11984 | 1218 | 1.2 | 0.46124 |  | 1.464 |  | 5694 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.05030020 | 19.5 | 118 | 20 | 8.6 | 15778 | 1603 | 1.58 | 0.21835 |  | 1.373 |  | 7275 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.05030021 | 19.5 | 118 | 21 | 8.6 | 16190 | 1645 | 1.62 | 0.35241 |  | 1.485 |  | 7746 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06004010 | 23.5 | 15.5 | 10 | 4.6 | 1014 | 773 | 0.1 | 0.00076924 |  | 1.376 |  | 468 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06004011 | 23.5 | 15.5 | 11 | 4.6 | 1270 | 968 | 0.13 | 0.0021088 |  | 1.437 |  | 598 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06004015 | 23.5 | 15.5 | 15 | 6.6 | 1624 | 1237 | 0.16 | 0.002165 |  | 1.361 |  | 746 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06004016 | 23.5 | 15.5 | 16 | 6.6 | 1753 | 1336 | 0.18 | 0.0080301 |  | 1.468 |  | 834 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06004020 | 23.5 | 15.5 | 20 | 8.6 | 2271 | 1731 | 0.23 | 0.0035544 |  | 1.361 |  | 1043 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06004021 | 23.5 | 15.5 | 21 | 8.6 | 2404 | 1832 | 0.24 | 0.0054132 |  | 1.493 |  | 1153 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06005010 | 23.5 | 19.5 | 10 | 4.6 | 1268 | 773 | 0.13 | 0.0013751 |  | 1.376 |  | 585 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06005011 | 23.5 | 19.5 | 11 | 4.6 | 1586 | 967 | 0.16 | 0.0034202 |  | 1.437 |  | 747 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06005015 | 23.5 | 19.5 | 15 | 6.6 | 2032 | 1239 | 0.2 | 0.0034649 |  | 1.361 |  | 933 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06005016 | 23.5 | 19.5 | 16 | 6.6 | 2190 | 1335 | 0.22 | 0.012193 |  | 1.468 |  | 1042 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06005020 | 23.5 | 19.5 | 20 | 8.6 | 2839 | 1731 | 0.28 | 0.0053588 |  | 1.361 |  | 1304 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06005021 | 23.5 | 19.5 | 21 | 8.6 | 3004 | 1831 | 0.3 | 0.0086584 |  | 1.493 |  | 1441 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06006010 | 23.5 | 23.5 | 10 | 4.6 | 1521 | 773 | 0.15 | 0.0019326 |  | 1.376 |  | 702 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06006011 | 23.5 | 23.5 | 11 | 4.6 | 1903 | 967 | 0.19 | 0.0051198 |  | 1.437 |  | 896 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06006015 | 23.5 | 23.5 | 15 | 6.6 | 2439 | 1239 | 0.24 | 0.005099 |  | 1.361 |  | 1120 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06006016 | 23.5 | 23.5 | 16 | 6.6 | 2627 | 1335 | 0.26 | 0.017286 |  | 1.468 |  | 1250 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06006020 | 23.5 | 23.5 | 20 | 8.6 | 3408 | 1731 | 0.34 | 0.0080207 |  | 1.361 |  | 1565 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06006021 | 23.5 | 23.5 | 21 | 8.6 | 3604 | 1831 | 0.36 | 0.012735 |  | 1.493 |  | 1729 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06007010 | 23.5 | 27.5 | 10 | 4.6 | 1775 | 773 | 0.18 | 0.0029084 |  | 1.376 |  | 819 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06007011 | 23.5 | 27.5 | 11 | 4.6 | 2221 | 967 | 0.22 | 0.0072402 |  | 1.437 |  | 1046 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06007015 | 23.5 | 27.5 | 15 | 6.6 | 2844 | 1238 | 0.28 | 0.0070808 |  | 1.361 |  | 1306 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06007016 | 23.5 | 27.5 | 16 | 6.6 | 3067 | 1335 | 0.31 | 0.024897 |  | 1.468 |  | 1459 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06007020 | 23.5 | 27.5 | 20 | 8.6 | 3976 | 1731 | 0.4 | 0.011256 |  | 1.361 |  | 1826 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06007021 | 23.5 | 27.5 | 21 | 8.6 | 4205 | 1831 | 0.42 | 0.017676 |  | 1.493 |  | 2017 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06008010 | 23.5 | 31.5 | 10 | 4.6 | 2028 | 773 | 0.2 | 0.0037545 |  | 1.376 |  | 936 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06008011 | 23.5 | 31.5 | 11 | 4.6 | 2538 | 967 | 0.25 | 0.0098125 |  | 1.437 |  | 1195 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06008015 | 23.5 | 31.5 | 15 | 6.6 | 3251 | 1239 | 0.33 | 0.010008 |  | 1.361 |  | 1493 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06008016 | 23.5 | 31.5 | 16 | 6.6 | 3504 | 1335 | 0.35 | 0.032154 |  | 1.468 |  | 1667 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06008020 | 23.5 | 31.5 | 20 | 8.6 | 4542 | 1731 | 0.45 | 0.014443 |  | 1.361 |  | 2086 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06008021 | 23.5 | 31.5 | 21 | 8.6 | 4807 | 1831 | 0.48 | 0.023512 |  | 1.493 |  | 2306 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06009010 | 23.5 | 35.5 | 10 | 4.6 | 2282 | 773 | 0.23 | 0.0051517 |  | 1.376 |  | 1053 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06009011 | 23.5 | 35.5 | 11 | 4.6 | 2856 | 967 | 0.29 | 0.013749 |  | 1.437 |  | 1345 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06009015 | 23.5 | 35.5 | 15 | 6.6 | 3656 | 1238 | 0.37 | 0.012805 |  | 1.361 |  | 1679 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06009016 | 23.5 | 35.5 | 16 | 6.6 | 3943 | 1335 | 0.39 | 0.04042 |  | 1.468 |  | 1876 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06009020 | 23.5 | 35.5 | 20 | 8.6 | 5110 | 1731 | 0.51 | 0.01878 |  | 1.361 |  | 2347 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06009021 | 23.5 | 35.5 | 21 | 8.6 | 5407 | 1831 | 0.54 | 0.030273 |  | 1.493 |  | 2594 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06010010 | 23.5 | 39.5 | 10 | 4.6 | 2535 | 773 | 0.25 | 0.0063246 |  | 1.376 |  | 1170 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06010011 | 23.5 | 39.5 | 11 | 4.6 | 3173 | 967 | 0.32 | 0.017445 |  | 1.437 |  | 1494 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06010015 | 23.5 | 39.5 | 15 | 6.6 | 4063 | 1238 | 0.41 | 0.015987 |  | 1.361 |  | 1866 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06010016 | 23.5 | 39.5 | 16 | 6.6 | 4380 | 1335 | 0.44 | 0.052016 |  | 1.468 |  | 2084 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06010020 | 23.5 | 39.5 | 20 | 8.6 | 5679 | 1731 | 0.57 | 0.023734 |  | 1.361 |  | 2608 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06010021 | 23.5 | 39.5 | 21 | 8.6 | 6008 | 1831 | 0.6 | 0.037986 |  | 1.493 |  | 2882 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06011010 | 23.5 | 43.5 | 10 | 4.6 | 2789 | 773 | 0.28 | 0.0081912 |  | 1.376 |  | 1287 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06011011 | 23.5 | 43.5 | 11 | 4.6 | 3489 | 967 | 0.35 | 0.021684 |  | 1.437 |  | 1643 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06011015 | 23.5 | 43.5 | 15 | 6.6 | 4470 | 1239 | 0.45 | 0.019567 |  | 1.361 |  | 2053 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06011016 | 23.5 | 43.5 | 16 | 6.6 | 4818 | 1335 | 0.48 | 0.062606 |  | 1.468 |  | 2292 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06011020 | 23.5 | 43.5 | 20 | 8.6 | 6247 | 1731 | 0.62 | 0.028414 |  | 1.361 |  | 2869 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06011021 | 23.5 | 43.5 | 21 | 8.6 | 6608 | 1831 | 0.66 | 0.04668 |  | 1.493 |  | 3170 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06012010 | 23.5 | 47 | 10 | 4.6 | 3042 | 773 | 0.3 | 0.0097267 |  | 1.376 |  | 1404 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06012011 | 23.5 | 47 | 11 | 4.6 | 3807 | 967 | 0.38 | 0.026495 |  | 1.437 |  | 1793 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06012015 | 23.5 | 47 | 15 | 6.6 | 4875 | 1238 | 0.49 | 0.023556 |  | 1.361 |  | 2239 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06012016 | 23.5 | 47 | 16 | 6.6 | 5257 | 1335 | 0.53 | 0.077101 |  | 1.468 |  | 2501 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06012020 | 23.5 | 47 | 20 | 8.6 | 6815 | 1731 | 0.68 | 0.034548 |  | 1.361 |  | 3130 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06012021 | 23.5 | 47 | 21 | 8.6 | 7209 | 1831 | 0.72 | 0.056381 |  | 1.493 |  | 3458 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06014010 | 23.5 | 55 | 10 | 4.6 | 3549 | 773 | 0.35 | 0.01404 |  | 1.376 |  | 1638 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06014011 | 23.5 | 55 | 11 | 4.6 | 4442 | 967 | 0.44 | 0.037938 |  | 1.437 |  | 2092 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06014015 | 23.5 | 55 | 15 | 6.6 | 5687 | 1238 | 0.57 | 0.0328 |  | 1.361 |  | 2612 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06014016 | 23.5 | 55 | 16 | 6.6 | 6133 | 1335 | 0.61 | 0.10426 |  | 1.468 |  | 2918 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06014020 | 23.5 | 55 | 20 | 8.6 | 7950 | 1731 | 0.8 | 0.048797 |  | 1.361 |  | 3651 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06014021 | 23.5 | 55 | 21 | 8.6 | 8411 | 1831 | 0.84 | 0.078909 |  | 1.493 |  | 4035 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06016010 | 23.5 | 63 | 10 | 4.6 | 4056 | 773 | 0.41 | 0.020253 |  | 1.376 |  | 1872 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06016011 | 23.5 | 63 | 11 | 4.6 | 5075 | 967 | 0.51 | 0.053925 |  | 1.437 |  | 2390 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06016015 | 23.5 | 63 | 15 | 6.6 | 6502 | 1239 | 0.65 | 0.043802 |  | 1.361 |  | 2986 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06016016 | 23.5 | 63 | 16 | 6.6 | 7008 | 1335 | 0.7 | 0.13986 |  | 1.468 |  | 3334 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06016020 | 23.5 | 63 | 20 | 8.6 | 9086 | 1731 | 0.91 | 0.064387 |  | 1.361 |  | 4173 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06016021 | 23.5 | 63 | 21 | 8.6 | 9612 | 1831 | 0.96 | 0.10577 |  | 1.493 |  | 4611 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06018010 | 23.5 | 71 | 10 | 4.6 | 4563 | 773 | 0.46 | 0.026772 |  | 1.376 |  | 2106 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06018011 | 23.5 | 71 | 11 | 4.6 | 5710 | 967 | 0.57 | 0.071102 |  | 1.437 |  | 2689 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06018015 | 23.5 | 71 | 15 | 6.6 | 7314 | 1239 | 0.73 | 0.056642 |  | 1.361 |  | 3359 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06018016 | 23.5 | 71 | 16 | 6.6 | 7884 | 1335 | 0.79 | 0.18129 |  | 1.468 |  | 3751 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06018020 | 23.5 | 71 | 20 | 8.6 | 10221 | 1731 | 1.02 | 0.082402 |  | 1.361 |  | 4694 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06018021 | 23.5 | 71 | 21 | 8.6 | 10815 | 1831 | 1.08 | 0.13716 |  | 1.493 |  | 5188 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06020010 | 23.5 | 78.5 | 10 | 4.6 | 5070 | 773 | 0.51 | 0.034428 |  | 1.376 |  | 2340 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06020011 | 23.5 | 78.5 | 11 | 4.6 | 6345 | 967 | 0.63 | 0.091284 |  | 1.437 |  | 2988 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06020015 | 23.5 | 78.5 | 15 | 6.6 | 8126 | 1238 | 0.81 | 0.071396 |  | 1.361 |  | 3732 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06020016 | 23.5 | 78.5 | 16 | 6.6 | 8761 | 1335 | 0.88 | 0.22873 |  | 1.468 |  | 4168 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06020020 | 23.5 | 78.5 | 20 | 8.6 | 11357 | 1731 | 1.14 | 0.1047 |  | 1.361 |  | 5216 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06020021 | 23.5 | 78.5 | 21 | 8.6 | 12016 | 1831 | 1.2 | 0.17326 |  | 1.493 |  | 5764 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06022010 | 23.5 | 86.5 | 10 | 4.6 | 5577 | 773 | 0.56 | 0.043289 |  | 1.376 |  | 2574 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06022011 | 23.5 | 86.5 | 11 | 4.6 | 6980 | 967 | 0.7 | 0.11773 |  | 1.437 |  | 3287 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06022015 | 23.5 | 86.5 | 15 | 6.6 | 8938 | 1238 | 0.89 | 0.088138 |  | 1.361 |  | 4105 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06022016 | 23.5 | 86.5 | 16 | 6.6 | 9637 | 1335 | 0.96 | 0.27675 |  | 1.468 |  | 4585 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06022020 | 23.5 | 86.5 | 20 | 8.6 | 12494 | 1731 | 1.25 | 0.128 |  | 1.361 |  | 5738 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06022021 | 23.5 | 86.5 | 21 | 8.6 | 13216 | 1831 | 1.32 | 0.21426 |  | 1.493 |  | 6340 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06024010 | 23.5 | 94.5 | 10 | 4.6 | 6084 | 773 | 0.61 | 0.05342 |  | 1.376 |  | 2808 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06024011 | 23.5 | 94.5 | 11 | 4.6 | 7615 | 967 | 0.76 | 0.14488 |  | 1.437 |  | 3586 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06024015 | 23.5 | 94.5 | 15 | 6.6 | 9751 | 1238 | 0.98 | 0.10906 |  | 1.361 |  | 4478 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06024016 | 23.5 | 94.5 | 16 | 6.6 | 10514 | 1335 | 1.05 | 0.33615 |  | 1.468 |  | 5002 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06024020 | 23.5 | 94.5 | 20 | 8.6 | 13629 | 1731 | 1.36 | 0.15396 |  | 1.361 |  | 6259 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06024021 | 23.5 | 94.5 | 21 | 8.6 | 14419 | 1831 | 1.44 | 0.26033 |  | 1.493 |  | 6917 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06026010 | 23.5 | 102.5 | 10 | 4.6 | 6591 | 773 | 0.66 | 0.064887 |  | 1.376 |  | 3042 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06026011 | 23.5 | 102.5 | 11 | 4.6 | 8248 | 967 | 0.82 | 0.17558 |  | 1.437 |  | 3884 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06026015 | 23.5 | 102.5 | 15 | 6.6 | 10565 | 1239 | 1.06 | 0.13021 |  | 1.361 |  | 4852 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06026016 | 23.5 | 102.5 | 16 | 6.6 | 11388 | 1335 | 1.14 | 0.40209 |  | 1.468 |  | 5418 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06026020 | 23.5 | 102.5 | 20 | 8.6 | 14765 | 1731 | 1.48 | 0.18507 |  | 1.361 |  | 6781 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06026021 | 23.5 | 102.5 | 21 | 8.6 | 15620 | 1831 | 1.56 | 0.31163 |  | 1.493 |  | 7493 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06028010 | 23.5 | 110 | 10 | 4.6 | 7098 | 773 | 0.71 | 0.077752 |  | 1.376 |  | 3276 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06028011 | 23.5 | 110 | 11 | 4.6 | 8883 | 967 | 0.89 | 0.21441 |  | 1.437 |  | 4183 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06028015 | 23.5 | 110 | 15 | 6.6 | 11377 | 1238 | 1.14 | 0.15357 |  | 1.361 |  | 5225 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06028016 | 23.5 | 110 | 16 | 6.6 | 12264 | 1335 | 1.23 | 0.47473 |  | 1.468 |  | 5835 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06028020 | 23.5 | 110 | 20 | 8.6 | 15900 | 1731 | 1.59 | 0.21678 |  | 1.361 |  | 7302 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06028021 | 23.5 | 110 | 21 | 8.6 | 16823 | 1831 | 1.68 | 0.36834 |  | 1.493 |  | 8070 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.06030010 | 23.5 | 118 | 10 | 4.6 | 7605 | 773 | 0.76 | 0.092077 |  | 1.376 |  | 3510 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.06030011 | 23.5 | 118 | 11 | 4.6 | 9518 | 967 | 0.95 | 0.25321 |  | 1.437 |  | 4482 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.06030015 | 23.5 | 118 | 15 | 6.6 | 12189 | 1238 | 1.22 | 0.17919 |  | 1.361 |  | 5598 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.06030016 | 23.5 | 118 | 16 | 6.6 | 13141 | 1335 | 1.31 | 0.54617 |  | 1.468 |  | 6252 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.06030020 | 23.5 | 118 | 20 | 8.6 | 17036 | 1731 | 1.7 | 0.25138 |  | 1.361 |  | 7824 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.06030021 | 23.5 | 118 | 21 | 8.6 | 18024 | 1831 | 1.8 | 0.43063 |  | 1.493 |  | 8646 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07004010 | 27.5 | 15.5 | 10 | 4.6 | 1085 | 827 | 0.11 | 0.00092626 |  | 1.366 |  | 499 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07004011 | 27.5 | 15.5 | 11 | 4.6 | 1351 | 1029 | 0.14 | 0.002435 |  | 1.436 |  | 636 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07004015 | 27.5 | 15.5 | 15 | 6.6 | 1724 | 1314 | 0.17 | 0.0024409 |  | 1.35 |  | 789 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07004016 | 27.5 | 15.5 | 16 | 6.6 | 1898 | 1446 | 0.19 | 0.0089402 |  | 1.472 |  | 904 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07004020 | 27.5 | 15.5 | 20 | 8.6 | 2407 | 1834 | 0.24 | 0.0038677 |  | 1.349 |  | 1101 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07004021 | 27.5 | 15.5 | 21 | 8.6 | 2643 | 2014 | 0.26 | 0.0063422 |  | 1.501 |  | 1271 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07005010 | 27.5 | 19.5 | 10 | 4.6 | 1356 | 827 | 0.14 | 0.0015874 |  | 1.366 |  | 624 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07005011 | 27.5 | 19.5 | 11 | 4.6 | 1689 | 1030 | 0.17 | 0.0038442 |  | 1.436 |  | 795 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07005015 | 27.5 | 19.5 | 15 | 6.6 | 2155 | 1314 | 0.22 | 0.0041816 |  | 1.35 |  | 986 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07005016 | 27.5 | 19.5 | 16 | 6.6 | 2372 | 1446 | 0.24 | 0.014487 |  | 1.472 |  | 1130 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07005020 | 27.5 | 19.5 | 20 | 8.6 | 3010 | 1835 | 0.3 | 0.0061434 |  | 1.349 |  | 1377 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07005021 | 27.5 | 19.5 | 21 | 8.6 | 3304 | 2014 | 0.33 | 0.01045 |  | 1.501 |  | 1589 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07006010 | 27.5 | 23.5 | 10 | 4.6 | 1628 | 827 | 0.16 | 0.0021885 |  | 1.366 |  | 749 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07006011 | 27.5 | 23.5 | 11 | 4.6 | 2026 | 1029 | 0.2 | 0.0056486 |  | 1.436 |  | 954 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07006015 | 27.5 | 23.5 | 15 | 6.6 | 2585 | 1313 | 0.26 | 0.0059686 |  | 1.35 |  | 1183 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07006016 | 27.5 | 23.5 | 16 | 6.6 | 2846 | 1446 | 0.28 | 0.020015 |  | 1.472 |  | 1356 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07006020 | 27.5 | 23.5 | 20 | 8.6 | 3611 | 1834 | 0.36 | 0.0089801 |  | 1.349 |  | 1652 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07006021 | 27.5 | 23.5 | 21 | 8.6 | 3963 | 2013 | 0.4 | 0.015669 |  | 1.501 |  | 1906 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07007010 | 27.5 | 27.5 | 10 | 4.6 | 1900 | 827 | 0.19 | 0.0032262 |  | 1.366 |  | 874 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07007011 | 27.5 | 27.5 | 11 | 4.6 | 2364 | 1029 | 0.24 | 0.0085471 |  | 1.436 |  | 1113 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07007015 | 27.5 | 27.5 | 15 | 6.6 | 3016 | 1313 | 0.3 | 0.0081073 |  | 1.35 |  | 1380 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07007016 | 27.5 | 27.5 | 16 | 6.6 | 3321 | 1446 | 0.33 | 0.028168 |  | 1.472 |  | 1582 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07007020 | 27.5 | 27.5 | 20 | 8.6 | 4213 | 1834 | 0.42 | 0.012394 |  | 1.349 |  | 1927 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07007021 | 27.5 | 27.5 | 21 | 8.6 | 4624 | 2013 | 0.46 | 0.021132 |  | 1.501 |  | 2224 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07008010 | 27.5 | 31.5 | 10 | 4.6 | 2169 | 826 | 0.22 | 0.0045043 |  | 1.366 |  | 998 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07008011 | 27.5 | 31.5 | 11 | 4.6 | 2702 | 1029 | 0.27 | 0.011357 |  | 1.436 |  | 1272 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07008015 | 27.5 | 31.5 | 15 | 6.6 | 3448 | 1314 | 0.34 | 0.01061 |  | 1.35 |  | 1578 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07008016 | 27.5 | 31.5 | 16 | 6.6 | 3795 | 1446 | 0.38 | 0.037813 |  | 1.472 |  | 1808 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07008020 | 27.5 | 31.5 | 20 | 8.6 | 4814 | 1834 | 0.48 | 0.0164 |  | 1.349 |  | 2202 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07008021 | 27.5 | 31.5 | 21 | 8.6 | 5285 | 2014 | 0.53 | 0.028549 |  | 1.501 |  | 2542 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07009010 | 27.5 | 35.5 | 10 | 4.6 | 2441 | 827 | 0.24 | 0.0055865 |  | 1.366 |  | 1123 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07009011 | 27.5 | 35.5 | 11 | 4.6 | 3040 | 1030 | 0.3 | 0.01466 |  | 1.436 |  | 1431 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07009015 | 27.5 | 35.5 | 15 | 6.6 | 3879 | 1314 | 0.39 | 0.014192 |  | 1.35 |  | 1775 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07009016 | 27.5 | 35.5 | 16 | 6.6 | 4270 | 1446 | 0.43 | 0.048985 |  | 1.472 |  | 2034 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07009020 | 27.5 | 35.5 | 20 | 8.6 | 5417 | 1835 | 0.54 | 0.021014 |  | 1.349 |  | 2478 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07009021 | 27.5 | 35.5 | 21 | 8.6 | 5944 | 2013 | 0.59 | 0.035993 |  | 1.501 |  | 2859 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07010010 | 27.5 | 39.5 | 10 | 4.6 | 2713 | 827 | 0.27 | 0.0073192 |  | 1.366 |  | 1248 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07010011 | 27.5 | 39.5 | 11 | 4.6 | 3377 | 1029 | 0.34 | 0.019558 |  | 1.436 |  | 1590 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07010015 | 27.5 | 39.5 | 15 | 6.6 | 4310 | 1314 | 0.43 | 0.017544 |  | 1.35 |  | 1972 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07010016 | 27.5 | 39.5 | 16 | 6.6 | 4744 | 1446 | 0.47 | 0.059217 |  | 1.472 |  | 2260 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07010020 | 27.5 | 39.5 | 20 | 8.6 | 6018 | 1834 | 0.6 | 0.02625 |  | 1.349 |  | 2753 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07010021 | 27.5 | 39.5 | 21 | 8.6 | 6605 | 2013 | 0.66 | 0.045749 |  | 1.501 |  | 3177 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07011010 | 27.5 | 43.5 | 10 | 4.6 | 2985 | 827 | 0.3 | 0.0093337 |  | 1.366 |  | 1373 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07011011 | 27.5 | 43.5 | 11 | 4.6 | 3715 | 1029 | 0.37 | 0.024072 |  | 1.436 |  | 1749 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07011015 | 27.5 | 43.5 | 15 | 6.6 | 4740 | 1313 | 0.47 | 0.021296 |  | 1.35 |  | 2169 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07011016 | 27.5 | 43.5 | 16 | 6.6 | 5218 | 1446 | 0.52 | 0.073258 |  | 1.472 |  | 2486 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07011020 | 27.5 | 43.5 | 20 | 8.6 | 6619 | 1834 | 0.66 | 0.032121 |  | 1.349 |  | 3028 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07011021 | 27.5 | 43.5 | 21 | 8.6 | 7266 | 2013 | 0.73 | 0.056806 |  | 1.501 |  | 3495 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07012010 | 27.5 | 47 | 10 | 4.6 | 3256 | 827 | 0.33 | 0.011644 |  | 1.366 |  | 1498 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07012011 | 27.5 | 47 | 11 | 4.6 | 4053 | 1029 | 0.41 | 0.030553 |  | 1.436 |  | 1908 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07012015 | 27.5 | 47 | 15 | 6.6 | 5171 | 1313 | 0.52 | 0.02644 |  | 1.35 |  | 2366 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07012016 | 27.5 | 47 | 16 | 6.6 | 5693 | 1446 | 0.57 | 0.088923 |  | 1.472 |  | 2712 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07012020 | 27.5 | 47 | 20 | 8.6 | 7223 | 1835 | 0.72 | 0.038641 |  | 1.349 |  | 3304 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07012021 | 27.5 | 47 | 21 | 8.6 | 7926 | 2013 | 0.79 | 0.067527 |  | 1.501 |  | 3812 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07014010 | 27.5 | 55 | 10 | 4.6 | 3798 | 827 | 0.38 | 0.016386 |  | 1.366 |  | 1747 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07014011 | 27.5 | 55 | 11 | 4.6 | 4728 | 1029 | 0.47 | 0.042908 |  | 1.436 |  | 2226 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07014015 | 27.5 | 55 | 15 | 6.6 | 6034 | 1314 | 0.6 | 0.036227 |  | 1.35 |  | 2761 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07014016 | 27.5 | 55 | 16 | 6.6 | 6642 | 1446 | 0.66 | 0.12162 |  | 1.472 |  | 3164 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07014020 | 27.5 | 55 | 20 | 8.6 | 8425 | 1834 | 0.84 | 0.053678 |  | 1.349 |  | 3854 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07014021 | 27.5 | 55 | 21 | 8.6 | 9248 | 2013 | 0.92 | 0.094125 |  | 1.501 |  | 4448 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07016010 | 27.5 | 63 | 10 | 4.6 | 4341 | 827 | 0.43 | 0.022142 |  | 1.366 |  | 1997 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07016011 | 27.5 | 63 | 11 | 4.6 | 5404 | 1029 | 0.54 | 0.059971 |  | 1.436 |  | 2544 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07016015 | 27.5 | 63 | 15 | 6.6 | 6895 | 1313 | 0.69 | 0.049158 |  | 1.35 |  | 3155 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07016016 | 27.5 | 63 | 16 | 6.6 | 7590 | 1446 | 0.76 | 0.16421 |  | 1.472 |  | 3616 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07016020 | 27.5 | 63 | 20 | 8.6 | 9630 | 1835 | 0.96 | 0.071463 |  | 1.349 |  | 4405 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07016021 | 27.5 | 63 | 21 | 8.6 | 10568 | 2013 | 1.06 | 0.1281 |  | 1.501 |  | 5083 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07018010 | 27.5 | 71 | 10 | 4.6 | 4882 | 827 | 0.49 | 0.03012 |  | 1.366 |  | 2246 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07018011 | 27.5 | 71 | 11 | 4.6 | 6079 | 1029 | 0.61 | 0.080622 |  | 1.436 |  | 2862 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07018015 | 27.5 | 71 | 15 | 6.6 | 7758 | 1314 | 0.78 | 0.064354 |  | 1.35 |  | 3550 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07018016 | 27.5 | 71 | 16 | 6.6 | 8539 | 1446 | 0.85 | 0.20907 |  | 1.472 |  | 4068 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07018020 | 27.5 | 71 | 20 | 8.6 | 10832 | 1834 | 1.08 | 0.092093 |  | 1.349 |  | 4955 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07018021 | 27.5 | 71 | 21 | 8.6 | 11890 | 2013 | 1.19 | 0.16536 |  | 1.501 |  | 5719 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07020010 | 27.5 | 78.5 | 10 | 4.6 | 5426 | 827 | 0.54 | 0.038288 |  | 1.366 |  | 2496 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07020011 | 27.5 | 78.5 | 11 | 4.6 | 6755 | 1029 | 0.68 | 0.10511 |  | 1.436 |  | 3180 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07020015 | 27.5 | 78.5 | 15 | 6.6 | 8619 | 1314 | 0.86 | 0.080107 |  | 1.35 |  | 3944 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07020016 | 27.5 | 78.5 | 16 | 6.6 | 9488 | 1446 | 0.95 | 0.26543 |  | 1.472 |  | 4520 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07020020 | 27.5 | 78.5 | 20 | 8.6 | 12037 | 1834 | 1.2 | 0.11566 |  | 1.349 |  | 5506 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07020021 | 27.5 | 78.5 | 21 | 8.6 | 13211 | 2013 | 1.32 | 0.20812 |  | 1.501 |  | 6354 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07022010 | 27.5 | 86.5 | 10 | 4.6 | 5969 | 827 | 0.6 | 0.049197 |  | 1.366 |  | 2746 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07022011 | 27.5 | 86.5 | 11 | 4.6 | 7430 | 1029 | 0.74 | 0.13042 |  | 1.436 |  | 3498 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07022015 | 27.5 | 86.5 | 15 | 6.6 | 9480 | 1313 | 0.95 | 0.099885 |  | 1.35 |  | 4338 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07022016 | 27.5 | 86.5 | 16 | 6.6 | 10437 | 1446 | 1.04 | 0.32325 |  | 1.472 |  | 4972 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07022020 | 27.5 | 86.5 | 20 | 8.6 | 13241 | 1834 | 1.32 | 0.14225 |  | 1.349 |  | 6057 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07022021 | 27.5 | 86.5 | 21 | 8.6 | 14531 | 2013 | 1.45 | 0.25658 |  | 1.501 |  | 6989 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07024010 | 27.5 | 94.5 | 10 | 4.6 | 6511 | 827 | 0.65 | 0.06008 |  | 1.366 |  | 2995 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07024011 | 27.5 | 94.5 | 11 | 4.6 | 8106 | 1029 | 0.81 | 0.16287 |  | 1.436 |  | 3816 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07024015 | 27.5 | 94.5 | 15 | 6.6 | 10343 | 1314 | 1.03 | 0.11996 |  | 1.35 |  | 4733 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07024016 | 27.5 | 94.5 | 16 | 6.6 | 11386 | 1446 | 1.14 | 0.39421 |  | 1.472 |  | 5424 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07024020 | 27.5 | 94.5 | 20 | 8.6 | 14443 | 1834 | 1.44 | 0.17196 |  | 1.349 |  | 6607 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07024021 | 27.5 | 94.5 | 21 | 8.6 | 15853 | 2013 | 1.59 | 0.31472 |  | 1.501 |  | 7625 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07026010 | 27.5 | 102.5 | 10 | 4.6 | 7054 | 827 | 0.71 | 0.074249 |  | 1.366 |  | 3245 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07026011 | 27.5 | 102.5 | 11 | 4.6 | 8781 | 1029 | 0.88 | 0.19985 |  | 1.436 |  | 4134 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07026015 | 27.5 | 102.5 | 15 | 6.6 | 11204 | 1313 | 1.12 | 0.14465 |  | 1.35 |  | 5127 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07026016 | 27.5 | 102.5 | 16 | 6.6 | 12334 | 1446 | 1.23 | 0.46574 |  | 1.472 |  | 5876 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07026020 | 27.5 | 102.5 | 20 | 8.6 | 15648 | 1834 | 1.56 | 0.20487 |  | 1.349 |  | 7158 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07026021 | 27.5 | 102.5 | 21 | 8.6 | 17173 | 2013 | 1.72 | 0.37556 |  | 1.501 |  | 8260 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07028010 | 27.5 | 110 | 10 | 4.6 | 7595 | 827 | 0.76 | 0.088135 |  | 1.366 |  | 3494 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07028011 | 27.5 | 110 | 11 | 4.6 | 9457 | 1029 | 0.95 | 0.2416 |  | 1.436 |  | 4452 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07028015 | 27.5 | 110 | 15 | 6.6 | 12068 | 1314 | 1.21 | 0.17204 |  | 1.35 |  | 5522 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07028016 | 27.5 | 110 | 16 | 6.6 | 13283 | 1446 | 1.33 | 0.55208 |  | 1.472 |  | 6328 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07028020 | 27.5 | 110 | 20 | 8.6 | 16850 | 1834 | 1.69 | 0.24384 |  | 1.349 |  | 7708 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07028021 | 27.5 | 110 | 21 | 8.6 | 18496 | 2013 | 1.85 | 0.4427 |  | 1.501 |  | 8896 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.07030010 | 27.5 | 118 | 10 | 4.6 | 8139 | 827 | 0.81 | 0.10352 |  | 1.366 |  | 3744 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.07030011 | 27.5 | 118 | 11 | 4.6 | 10132 | 1029 | 1.01 | 0.28318 |  | 1.436 |  | 4770 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.07030015 | 27.5 | 118 | 15 | 6.6 | 12929 | 1314 | 1.29 | 0.19927 |  | 1.35 |  | 5916 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.07030016 | 27.5 | 118 | 16 | 6.6 | 14232 | 1446 | 1.42 | 0.63805 |  | 1.472 |  | 6780 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.07030020 | 27.5 | 118 | 20 | 8.6 | 18055 | 1834 | 1.81 | 0.28363 |  | 1.349 |  | 8259 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.07030021 | 27.5 | 118 | 21 | 8.6 | 19816 | 2013 | 1.98 | 0.51632 |  | 1.501 |  | 9531 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09004010 | 35.5 | 15.5 | 10 | 4.6 | 1198 | 913 | 0.12 | 0.0010975 |  | 1.348 |  | 548 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09004011 | 35.5 | 15.5 | 11 | 4.6 | 1494 | 1138 | 0.15 | 0.0027841 |  | 1.434 |  | 703 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09004015 | 35.5 | 15.5 | 15 | 6.6 | 1868 | 1423 | 0.19 | 0.0030418 |  | 1.326 |  | 848 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09004016 | 35.5 | 15.5 | 16 | 6.6 | 2173 | 1656 | 0.22 | 0.011962 |  | 1.48 |  | 1038 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09004020 | 35.5 | 15.5 | 20 | 8.6 | 2606 | 1986 | 0.26 | 0.0045338 |  | 1.326 |  | 1183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09004021 | 35.5 | 15.5 | 21 | 8.6 | 3118 | 2376 | 0.31 | 0.0089836 |  | 1.518 |  | 1508 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09005010 | 35.5 | 19.5 | 10 | 4.6 | 1498 | 913 | 0.15 | 0.0018145 |  | 1.348 |  | 685 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09005011 | 35.5 | 19.5 | 11 | 4.6 | 1868 | 1139 | 0.19 | 0.0047639 |  | 1.434 |  | 879 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09005015 | 35.5 | 19.5 | 15 | 6.6 | 2335 | 1423 | 0.23 | 0.0045649 |  | 1.326 |  | 1060 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09005016 | 35.5 | 19.5 | 16 | 6.6 | 2717 | 1656 | 0.27 | 0.018297 |  | 1.48 |  | 1298 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09005020 | 35.5 | 19.5 | 20 | 8.6 | 3258 | 1986 | 0.33 | 0.00742 |  | 1.326 |  | 1479 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09005021 | 35.5 | 19.5 | 21 | 8.6 | 3897 | 2376 | 0.39 | 0.014531 |  | 1.518 |  | 1885 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09006010 | 35.5 | 23.5 | 10 | 4.6 | 1795 | 912 | 0.18 | 0.0027464 |  | 1.348 |  | 821 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09006011 | 35.5 | 23.5 | 11 | 4.6 | 2243 | 1139 | 0.22 | 0.0067812 |  | 1.434 |  | 1055 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09006015 | 35.5 | 23.5 | 15 | 6.6 | 2802 | 1423 | 0.28 | 0.0069056 |  | 1.326 |  | 1272 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09006016 | 35.5 | 23.5 | 16 | 6.6 | 3262 | 1657 | 0.33 | 0.027703 |  | 1.48 |  | 1558 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09006020 | 35.5 | 23.5 | 20 | 8.6 | 3908 | 1985 | 0.39 | 0.01052 |  | 1.326 |  | 1774 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09006021 | 35.5 | 23.5 | 21 | 8.6 | 4677 | 2376 | 0.47 | 0.021525 |  | 1.518 |  | 2262 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09007010 | 35.5 | 27.5 | 10 | 4.6 | 2095 | 912 | 0.21 | 0.0039095 |  | 1.348 |  | 958 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09007011 | 35.5 | 27.5 | 11 | 4.6 | 2617 | 1140 | 0.26 | 0.0099578 |  | 1.434 |  | 1231 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09007015 | 35.5 | 27.5 | 15 | 6.6 | 3269 | 1423 | 0.33 | 0.0097754 |  | 1.326 |  | 1484 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09007016 | 35.5 | 27.5 | 16 | 6.6 | 3804 | 1656 | 0.38 | 0.03722 |  | 1.48 |  | 1817 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09007020 | 35.5 | 27.5 | 20 | 8.6 | 4560 | 1986 | 0.46 | 0.014831 |  | 1.326 |  | 2070 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09007021 | 35.5 | 27.5 | 21 | 8.6 | 5456 | 2376 | 0.55 | 0.030018 |  | 1.518 |  | 2639 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09008010 | 35.5 | 31.5 | 10 | 4.6 | 2395 | 912 | 0.24 | 0.0053196 |  | 1.348 |  | 1095 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09008011 | 35.5 | 31.5 | 11 | 4.6 | 2989 | 1139 | 0.3 | 0.013874 |  | 1.434 |  | 1406 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09008015 | 35.5 | 31.5 | 15 | 6.6 | 3736 | 1423 | 0.37 | 0.012522 |  | 1.326 |  | 1696 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09008016 | 35.5 | 31.5 | 16 | 6.6 | 4348 | 1657 | 0.43 | 0.048251 |  | 1.48 |  | 2077 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09008020 | 35.5 | 31.5 | 20 | 8.6 | 5212 | 1986 | 0.52 | 0.019202 |  | 1.326 |  | 2366 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09008021 | 35.5 | 31.5 | 21 | 8.6 | 6236 | 2376 | 0.62 | 0.038823 |  | 1.518 |  | 3016 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09009010 | 35.5 | 35.5 | 10 | 4.6 | 2694 | 912 | 0.27 | 0.0069919 |  | 1.348 |  | 1232 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09009011 | 35.5 | 35.5 | 11 | 4.6 | 3363 | 1139 | 0.34 | 0.018581 |  | 1.434 |  | 1582 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09009015 | 35.5 | 35.5 | 15 | 6.6 | 4203 | 1423 | 0.42 | 0.016404 |  | 1.326 |  | 1908 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09009016 | 35.5 | 35.5 | 16 | 6.6 | 4891 | 1656 | 0.49 | 0.063353 |  | 1.48 |  | 2336 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09009020 | 35.5 | 35.5 | 20 | 8.6 | 5861 | 1985 | 0.59 | 0.025014 |  | 1.326 |  | 2661 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09009021 | 35.5 | 35.5 | 21 | 8.6 | 7015 | 2376 | 0.7 | 0.050287 |  | 1.518 |  | 3393 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09010010 | 35.5 | 39.5 | 10 | 4.6 | 2994 | 913 | 0.3 | 0.0089407 |  | 1.348 |  | 1369 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09010011 | 35.5 | 39.5 | 11 | 4.6 | 3737 | 1139 | 0.37 | 0.022942 |  | 1.434 |  | 1758 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09010015 | 35.5 | 39.5 | 15 | 6.6 | 4670 | 1423 | 0.47 | 0.020868 |  | 1.326 |  | 2120 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09010016 | 35.5 | 39.5 | 16 | 6.6 | 5435 | 1657 | 0.54 | 0.077806 |  | 1.48 |  | 2596 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09010020 | 35.5 | 39.5 | 20 | 8.6 | 6513 | 1985 | 0.65 | 0.03072 |  | 1.326 |  | 2957 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09010021 | 35.5 | 39.5 | 21 | 8.6 | 7794 | 2376 | 0.78 | 0.063392 |  | 1.518 |  | 3770 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09011010 | 35.5 | 43.5 | 10 | 4.6 | 3293 | 912 | 0.33 | 0.01118 |  | 1.348 |  | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09011011 | 35.5 | 43.5 | 11 | 4.6 | 4111 | 1139 | 0.41 | 0.029202 |  | 1.434 |  | 1934 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09011015 | 35.5 | 43.5 | 15 | 6.6 | 5137 | 1423 | 0.51 | 0.024968 |  | 1.326 |  | 2332 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09011016 | 35.5 | 43.5 | 16 | 6.6 | 5979 | 1657 | 0.6 | 0.09703 |  | 1.48 |  | 2856 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09011020 | 35.5 | 43.5 | 20 | 8.6 | 7165 | 1985 | 0.72 | 0.0381 |  | 1.326 |  | 3253 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09011021 | 35.5 | 43.5 | 21 | 8.6 | 8574 | 2376 | 0.86 | 0.078185 |  | 1.518 |  | 4147 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09012010 | 35.5 | 47 | 10 | 4.6 | 3593 | 913 | 0.36 | 0.013724 |  | 1.348 |  | 1643 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09012011 | 35.5 | 47 | 11 | 4.6 | 4485 | 1139 | 0.45 | 0.036386 |  | 1.434 |  | 2110 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09012015 | 35.5 | 47 | 15 | 6.6 | 5604 | 1423 | 0.56 | 0.030537 |  | 1.326 |  | 2544 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09012016 | 35.5 | 47 | 16 | 6.6 | 6521 | 1656 | 0.65 | 0.11505 |  | 1.48 |  | 3115 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09012020 | 35.5 | 47 | 20 | 8.6 | 7815 | 1985 | 0.78 | 0.045201 |  | 1.326 |  | 3548 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09012021 | 35.5 | 47 | 21 | 8.6 | 9353 | 2376 | 0.94 | 0.094709 |  | 1.518 |  | 4524 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09014010 | 35.5 | 55 | 10 | 4.6 | 4192 | 913 | 0.42 | 0.019778 |  | 1.348 |  | 1917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09014011 | 35.5 | 55 | 11 | 4.6 | 5231 | 1139 | 0.52 | 0.051825 |  | 1.434 |  | 2461 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09014015 | 35.5 | 55 | 15 | 6.6 | 6538 | 1423 | 0.65 | 0.042306 |  | 1.326 |  | 2968 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09014016 | 35.5 | 55 | 16 | 6.6 | 7608 | 1656 | 0.76 | 0.16029 |  | 1.48 |  | 3634 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09014020 | 35.5 | 55 | 20 | 8.6 | 9119 | 1985 | 0.91 | 0.062768 |  | 1.326 |  | 4140 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09014021 | 35.5 | 55 | 21 | 8.6 | 10912 | 2376 | 1.09 | 0.13078 |  | 1.518 |  | 5278 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09016010 | 35.5 | 63 | 10 | 4.6 | 4789 | 912 | 0.48 | 0.027207 |  | 1.348 |  | 2190 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09016011 | 35.5 | 63 | 11 | 4.6 | 5979 | 1139 | 0.6 | 0.072958 |  | 1.434 |  | 2813 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09016015 | 35.5 | 63 | 15 | 6.6 | 7472 | 1423 | 0.75 | 0.057755 |  | 1.326 |  | 3392 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09016016 | 35.5 | 63 | 16 | 6.6 | 8697 | 1657 | 0.87 | 0.21382 |  | 1.48 |  | 4154 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09016020 | 35.5 | 63 | 20 | 8.6 | 10421 | 1985 | 1.04 | 0.083536 |  | 1.326 |  | 4731 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09016021 | 35.5 | 63 | 21 | 8.6 | 12471 | 2376 | 1.25 | 0.17623 |  | 1.518 |  | 6032 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09018010 | 35.5 | 71 | 10 | 4.6 | 5388 | 912 | 0.54 | 0.036109 |  | 1.348 |  | 2464 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09018011 | 35.5 | 71 | 11 | 4.6 | 6725 | 1139 | 0.67 | 0.095939 |  | 1.434 |  | 3164 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09018015 | 35.5 | 71 | 15 | 6.6 | 8406 | 1423 | 0.84 | 0.074237 |  | 1.326 |  | 3816 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09018016 | 35.5 | 71 | 16 | 6.6 | 9783 | 1657 | 0.98 | 0.2759 |  | 1.48 |  | 4673 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09018020 | 35.5 | 71 | 20 | 8.6 | 11725 | 1985 | 1.17 | 0.10762 |  | 1.326 |  | 5323 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09018021 | 35.5 | 71 | 21 | 8.6 | 14030 | 2376 | 1.4 | 0.22627 |  | 1.518 |  | 6786 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09020010 | 35.5 | 78.5 | 10 | 4.6 | 5987 | 912 | 0.6 | 0.046581 |  | 1.348 |  | 2738 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09020011 | 35.5 | 78.5 | 11 | 4.6 | 7474 | 1139 | 0.75 | 0.12598 |  | 1.434 |  | 3516 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09020015 | 35.5 | 78.5 | 15 | 6.6 | 9340 | 1423 | 0.93 | 0.093117 |  | 1.326 |  | 4240 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09020016 | 35.5 | 78.5 | 16 | 6.6 | 10870 | 1657 | 1.09 | 0.34681 |  | 1.48 |  | 5192 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09020020 | 35.5 | 78.5 | 20 | 8.6 | 13027 | 1985 | 1.3 | 0.13511 |  | 1.326 |  | 5914 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09020021 | 35.5 | 78.5 | 21 | 8.6 | 15589 | 2376 | 1.56 | 0.28706 |  | 1.518 |  | 7540 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09022010 | 35.5 | 86.5 | 10 | 4.6 | 6587 | 913 | 0.66 | 0.058715 |  | 1.348 |  | 3012 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09022011 | 35.5 | 86.5 | 11 | 4.6 | 8222 | 1139 | 0.82 | 0.15759 |  | 1.434 |  | 3868 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09022015 | 35.5 | 86.5 | 15 | 6.6 | 10274 | 1423 | 1.03 | 0.11665 |  | 1.326 |  | 4664 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09022016 | 35.5 | 86.5 | 16 | 6.6 | 11956 | 1656 | 1.2 | 0.4268 |  | 1.48 |  | 5711 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09022020 | 35.5 | 86.5 | 20 | 8.6 | 14329 | 1985 | 1.43 | 0.16613 |  | 1.326 |  | 6505 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09022021 | 35.5 | 86.5 | 21 | 8.6 | 17148 | 2376 | 1.71 | 0.35221 |  | 1.518 |  | 8294 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09024010 | 35.5 | 94.5 | 10 | 4.6 | 7186 | 913 | 0.72 | 0.072603 |  | 1.348 |  | 3286 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09024011 | 35.5 | 94.5 | 11 | 4.6 | 8968 | 1139 | 0.9 | 0.19769 |  | 1.434 |  | 4219 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09024015 | 35.5 | 94.5 | 15 | 6.6 | 11208 | 1423 | 1.12 | 0.14083 |  | 1.326 |  | 5088 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09024016 | 35.5 | 94.5 | 16 | 6.6 | 13043 | 1656 | 1.3 | 0.50851 |  | 1.48 |  | 6230 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09024020 | 35.5 | 94.5 | 20 | 8.6 | 15633 | 1985 | 1.56 | 0.20078 |  | 1.326 |  | 7097 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09024021 | 35.5 | 94.5 | 21 | 8.6 | 18707 | 2376 | 1.87 | 0.4295 |  | 1.518 |  | 9048 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09026010 | 35.5 | 102.5 | 10 | 4.6 | 7783 | 912 | 0.78 | 0.088332 |  | 1.348 |  | 3559 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09026011 | 35.5 | 102.5 | 11 | 4.6 | 9716 | 1139 | 0.97 | 0.23895 |  | 1.434 |  | 4571 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09026015 | 35.5 | 102.5 | 15 | 6.6 | 12141 | 1423 | 1.21 | 0.16768 |  | 1.326 |  | 5512 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09026016 | 35.5 | 102.5 | 16 | 6.6 | 14132 | 1657 | 1.41 | 0.60667 |  | 1.48 |  | 6750 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09026020 | 35.5 | 102.5 | 20 | 8.6 | 16935 | 1985 | 1.69 | 0.23914 |  | 1.326 |  | 7688 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09026021 | 35.5 | 102.5 | 21 | 8.6 | 20265 | 2376 | 2.03 | 0.51567 |  | 1.518 |  | 9802 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09028010 | 35.5 | 110 | 10 | 4.6 | 8382 | 912 | 0.84 | 0.10599 |  | 1.348 |  | 3833 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09028011 | 35.5 | 110 | 11 | 4.6 | 10462 | 1139 | 1.05 | 0.2902 |  | 1.434 |  | 4922 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09028015 | 35.5 | 110 | 15 | 6.6 | 13075 | 1423 | 1.31 | 0.20018 |  | 1.326 |  | 5936 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09028016 | 35.5 | 110 | 16 | 6.6 | 15218 | 1657 | 1.52 | 0.71463 |  | 1.48 |  | 7269 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09028020 | 35.5 | 110 | 20 | 8.6 | 18239 | 1985 | 1.82 | 0.28132 |  | 1.326 |  | 8280 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09028021 | 35.5 | 110 | 21 | 8.6 | 21824 | 2376 | 2.18 | 0.60568 |  | 1.518 |  | 10556 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In | Build-In Wall | BIWW.09030010 | 35.5 | 118 | 10 | 4.6 | 8981 | 912 | 0.9 | 0.12566 |  | 1.348 |  | 4107 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In | Build-In Wall | BIWW.09030011 | 35.5 | 118 | 11 | 4.6 | 11210 | 1139 | 1.12 | 0.34209 |  | 1.434 |  | 5274 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Build-In | Build-In Wall | BIWW.09030015 | 35.5 | 118 | 15 | 6.6 | 14009 | 1423 | 1.4 | 0.23287 |  | 1.326 |  | 6360 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In | Build-In Wall | BIWW.09030016 | 35.5 | 118 | 16 | 6.6 | 16305 | 1657 | 1.63 | 0.83263 |  | 1.48 |  | 7788 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Build-In | Build-In Wall | BIWW.09030020 | 35.5 | 118 | 20 | 8.6 | 19540 | 1985 | 1.95 | 0.32741 |  | 1.326 |  | 8871 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In | Build-In Wall | BIWW.09030021 | 35.5 | 118 | 21 | 8.6 | 23383 | 2376 | 2.34 | 0.70996 |  | 1.518 |  | 11310 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Knockonwood | KNOW.05506010 | 21.5 | 23.5 | 10 | 5 | 1415 | 719 | 0.14 | 0.0016922 |  | 1.407 |  | 660 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Knockonwood | KNOW.05506011 | 21.5 | 23.5 | 11 | 5 | 1500 | 762 | 0.15 | 0.0032565 |  | 1.487 |  | 718 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Knockonwood | KNOW.05506015 | 21.5 | 23.5 | 15 | 7 | 2160 | 1097 | 0.22 | 0.0042971 |  | 1.389 |  | 1001 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Knockonwood | KNOW.05506016 | 21.5 | 23.5 | 16 | 7 | 2225 | 1130 | 0.22 | 0.012424 |  | 1.48 |  | 1063 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Knockonwood | KNOW.05508010 | 21.5 | 31.5 | 10 | 5 | 1887 | 719 | 0.19 | 0.0034042 |  | 1.407 |  | 880 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Knockonwood | KNOW.05508011 | 21.5 | 31.5 | 11 | 5 | 2001 | 762 | 0.2 | 0.0064267 |  | 1.487 |  | 958 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Knockonwood | KNOW.05508015 | 21.5 | 31.5 | 15 | 7 | 2880 | 1097 | 0.29 | 0.0077715 |  | 1.389 |  | 1335 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Knockonwood | KNOW.05508016 | 21.5 | 31.5 | 16 | 7 | 2969 | 1131 | 0.3 | 0.023731 |  | 1.48 |  | 1418 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Knockonwood | KNOW.05510010 | 21.5 | 39.5 | 10 | 5 | 2359 | 719 | 0.24 | 0.0058534 |  | 1.407 |  | 1100 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Knockonwood | KNOW.05510011 | 21.5 | 39.5 | 11 | 5 | 2500 | 762 | 0.25 | 0.010958 |  | 1.487 |  | 1197 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Knockonwood | KNOW.05510015 | 21.5 | 39.5 | 15 | 7 | 3601 | 1098 | 0.36 | 0.012407 |  | 1.389 |  | 1669 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Knockonwood | KNOW.05510016 | 21.5 | 39.5 | 16 | 7 | 3710 | 1131 | 0.37 | 0.037008 |  | 1.48 |  | 1772 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Knockonwood | KNOW.05512010 | 21.5 | 47 | 10 | 5 | 2831 | 719 | 0.28 | 0.0085399 |  | 1.407 |  | 1320 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Knockonwood | KNOW.05512011 | 21.5 | 47 | 11 | 5 | 2999 | 762 | 0.3 | 0.017018 |  | 1.487 |  | 1436 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Knockonwood | KNOW.05512015 | 21.5 | 47 | 15 | 7 | 4321 | 1098 | 0.43 | 0.018277 |  | 1.389 |  | 2003 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Knockonwood | KNOW.05512016 | 21.5 | 47 | 16 | 7 | 4451 | 1131 | 0.45 | 0.055952 |  | 1.48 |  | 2126 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Knockonwood | KNOW.05514010 | 21.5 | 55 | 10 | 5 | 3303 | 719 | 0.33 | 0.012571 |  | 1.407 |  | 1540 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Knockonwood | KNOW.05514011 | 21.5 | 55 | 11 | 5 | 3501 | 762 | 0.35 | 0.024765 |  | 1.487 |  | 1676 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Knockonwood | KNOW.05514015 | 21.5 | 55 | 15 | 7 | 5042 | 1098 | 0.5 | 0.025451 |  | 1.389 |  | 2337 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Knockonwood | KNOW.05514016 | 21.5 | 55 | 16 | 7 | 5194 | 1131 | 0.52 | 0.076312 |  | 1.48 |  | 2481 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Knockonwood DBE | KNUF.02111015/DBE | 8.5 | 43.5 | 15 | 8.3 | 4116 | 1141 | 0.41 | 0.016325 |  | 1 |  | 1678 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Knockonwood DBE | KNUF.02113015/DBE | 8.5 | 51 | 15 | 8.3 | 5308 | 1245 | 0.53 | 0.027963 |  | 1 |  | 2164 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Knockonwood DBE | KNUF.02117015/DBE | 8.5 | 67 | 15 | 8.3 | 7077 | 1269 | 0.71 | 0.05282 |  | 1 |  | 2885 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Knockonwood DBE | KNUF.02121015/DBE | 8.5 | 82.5 | 15 | 8.3 | 8845 | 1284 | 0.88 | 0.084989 |  | 1 |  | 3606 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Maxi | MAXW.04406311/FT | 17.5 | 25 | 11 | 5.1 | 829 | 401 | 0.08 | 0.0010057 |  | 1.44 |  | 391 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04406311/WF | 17.5 | 25 | 11 | 5.1 | 709 | 343 | 0.07 | 0.00078068 |  | 1.44 |  | 334 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04406311/WT | 17.5 | 25 | 11 | 5.1 | 1014 | 491 | 0.1 | 0.0015368 |  | 1.439 |  | 478 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04406316/FT | 17.5 | 25 | 16 | 7.1 | 1182 | 572 | 0.12 | 0.0037779 |  | 1.455 |  | 560 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04406316/WF | 17.5 | 25 | 16 | 7.1 | 1048 | 507 | 0.1 | 0.0026377 |  | 1.457 |  | 497 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04406316/WT | 17.5 | 25 | 16 | 7.1 | 1512 | 732 | 0.15 | 0.0058661 |  | 1.462 |  | 718 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04406321/FT | 17.5 | 25 | 21 | 9.1 | 1518 | 734 | 0.15 | 0.0023043 |  | 1.467 |  | 722 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04406321/WF | 17.5 | 25 | 21 | 9.1 | 1301 | 629 | 0.13 | 0.0017416 |  | 1.472 |  | 620 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04406321/WT | 17.5 | 25 | 21 | 9.1 | 2018 | 976 | 0.2 | 0.0040483 |  | 1.48 |  | 964 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04408311/FT | 17.5 | 32.5 | 11 | 5.1 | 1220 | 448 | 0.12 | 0.0024951 |  | 1.44 |  | 575 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04408311/WF | 17.5 | 32.5 | 11 | 5.1 | 1042 | 383 | 0.1 | 0.0017706 |  | 1.44 |  | 491 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04408311/WT | 17.5 | 32.5 | 11 | 5.1 | 1494 | 549 | 0.15 | 0.0037998 |  | 1.439 |  | 704 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04408316/FT | 17.5 | 32.5 | 16 | 7.1 | 1739 | 639 | 0.17 | 0.0078057 |  | 1.455 |  | 824 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04408316/WF | 17.5 | 32.5 | 16 | 7.1 | 1544 | 567 | 0.15 | 0.0061049 |  | 1.457 |  | 732 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04408316/WT | 17.5 | 32.5 | 16 | 7.1 | 2226 | 817 | 0.22 | 0.012956 |  | 1.462 |  | 1057 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04408321/FT | 17.5 | 32.5 | 21 | 9.1 | 2235 | 821 | 0.22 | 0.0051609 |  | 1.467 |  | 1063 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04408321/WF | 17.5 | 32.5 | 21 | 9.1 | 1916 | 704 | 0.19 | 0.0038793 |  | 1.472 |  | 913 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04408321/WT | 17.5 | 32.5 | 21 | 9.1 | 2969 | 1090 | 0.3 | 0.0094488 |  | 1.48 |  | 1418 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04410311/FT | 17.5 | 40.5 | 11 | 5.1 | 1610 | 476 | 0.16 | 0.0048204 |  | 1.44 |  | 759 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04410311/WF | 17.5 | 40.5 | 11 | 5.1 | 1377 | 407 | 0.14 | 0.0037552 |  | 1.44 |  | 649 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04410311/WT | 17.5 | 40.5 | 11 | 5.1 | 1971 | 583 | 0.2 | 0.0073215 |  | 1.439 |  | 929 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04410316/FT | 17.5 | 40.5 | 16 | 7.1 | 2297 | 680 | 0.23 | 0.014638 |  | 1.455 |  | 1088 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04410316/WF | 17.5 | 40.5 | 16 | 7.1 | 2040 | 604 | 0.2 | 0.011134 |  | 1.457 |  | 967 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04410316/WT | 17.5 | 40.5 | 16 | 7.1 | 2940 | 870 | 0.29 | 0.023054 |  | 1.462 |  | 1396 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04410321/FT | 17.5 | 40.5 | 21 | 9.1 | 2952 | 874 | 0.3 | 0.0099278 |  | 1.467 |  | 1404 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04410321/WF | 17.5 | 40.5 | 21 | 9.1 | 2532 | 749 | 0.25 | 0.006971 |  | 1.472 |  | 1206 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04410321/WT | 17.5 | 40.5 | 21 | 9.1 | 3921 | 1160 | 0.39 | 0.016526 |  | 1.48 |  | 1873 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04412311/FT | 17.5 | 48.5 | 11 | 5.1 | 2000 | 496 | 0.2 | 0.0080996 |  | 1.44 |  | 943 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04412311/WF | 17.5 | 48.5 | 11 | 5.1 | 1712 | 424 | 0.17 | 0.0059865 |  | 1.44 |  | 807 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04412311/WT | 17.5 | 48.5 | 11 | 5.1 | 2451 | 607 | 0.25 | 0.012276 |  | 1.439 |  | 1155 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04412316/FT | 17.5 | 48.5 | 16 | 7.1 | 2854 | 707 | 0.29 | 0.023798 |  | 1.455 |  | 1352 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04412316/WF | 17.5 | 48.5 | 16 | 7.1 | 2534 | 628 | 0.25 | 0.017811 |  | 1.457 |  | 1201 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04412316/WT | 17.5 | 48.5 | 16 | 7.1 | 3654 | 905 | 0.37 | 0.038311 |  | 1.462 |  | 1735 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04412321/FT | 17.5 | 48.5 | 21 | 9.1 | 3667 | 909 | 0.37 | 0.015606 |  | 1.467 |  | 1744 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04412321/WF | 17.5 | 48.5 | 21 | 9.1 | 3144 | 779 | 0.31 | 0.011087 |  | 1.472 |  | 1498 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04412321/WT | 17.5 | 48.5 | 21 | 9.1 | 4874 | 1208 | 0.49 | 0.026878 |  | 1.48 |  | 2328 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04414311/FT | 17.5 | 56.5 | 11 | 5.1 | 2391 | 510 | 0.24 | 0.012444 |  | 1.44 |  | 1127 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04414311/WF | 17.5 | 56.5 | 11 | 5.1 | 2045 | 436 | 0.2 | 0.0088777 |  | 1.44 |  | 964 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04414311/WT | 17.5 | 56.5 | 11 | 5.1 | 2931 | 625 | 0.29 | 0.017678 |  | 1.439 |  | 1381 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04414316/FT | 17.5 | 56.5 | 16 | 7.1 | 3411 | 727 | 0.34 | 0.033452 |  | 1.455 |  | 1616 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04414316/WF | 17.5 | 56.5 | 16 | 7.1 | 3029 | 646 | 0.3 | 0.026216 |  | 1.457 |  | 1436 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04414316/WT | 17.5 | 56.5 | 16 | 7.1 | 4368 | 931 | 0.44 | 0.055299 |  | 1.462 |  | 2074 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04414321/FT | 17.5 | 56.5 | 21 | 9.1 | 4384 | 934 | 0.44 | 0.022747 |  | 1.467 |  | 2085 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04414321/WF | 17.5 | 56.5 | 21 | 9.1 | 3760 | 801 | 0.38 | 0.017151 |  | 1.472 |  | 1791 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04414321/WT | 17.5 | 56.5 | 21 | 9.1 | 5824 | 1241 | 0.58 | 0.03876 |  | 1.48 |  | 2782 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04416311/FT | 17.5 | 64 | 11 | 5.1 | 2783 | 520 | 0.28 | 0.017957 |  | 1.44 |  | 1312 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04416311/WF | 17.5 | 64 | 11 | 5.1 | 2380 | 445 | 0.24 | 0.013511 |  | 1.44 |  | 1122 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04416311/WT | 17.5 | 64 | 11 | 5.1 | 3408 | 637 | 0.34 | 0.02571 |  | 1.439 |  | 1606 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04416316/FT | 17.5 | 64 | 16 | 7.1 | 3969 | 742 | 0.4 | 0.047213 |  | 1.455 |  | 1880 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04416316/WF | 17.5 | 64 | 16 | 7.1 | 3523 | 659 | 0.35 | 0.036424 |  | 1.457 |  | 1670 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04416316/WT | 17.5 | 64 | 16 | 7.1 | 5082 | 950 | 0.51 | 0.075736 |  | 1.462 |  | 2413 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04416321/FT | 17.5 | 64 | 21 | 9.1 | 5101 | 954 | 0.51 | 0.031433 |  | 1.467 |  | 2426 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04416321/WF | 17.5 | 64 | 21 | 9.1 | 4375 | 818 | 0.44 | 0.023674 |  | 1.472 |  | 2084 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04416321/WT | 17.5 | 64 | 21 | 9.1 | 6777 | 1267 | 0.68 | 0.054668 |  | 1.48 |  | 3237 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04418311/FT | 17.5 | 72 | 11 | 5.1 | 3174 | 529 | 0.32 | 0.024741 |  | 1.44 |  | 1496 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04418311/WF | 17.5 | 72 | 11 | 5.1 | 2713 | 452 | 0.27 | 0.018101 |  | 1.44 |  | 1279 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04418311/WT | 17.5 | 72 | 11 | 5.1 | 3888 | 648 | 0.39 | 0.035624 |  | 1.439 |  | 1832 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04418316/FT | 17.5 | 72 | 16 | 7.1 | 4526 | 754 | 0.45 | 0.060952 |  | 1.455 |  | 2144 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04418316/WF | 17.5 | 72 | 16 | 7.1 | 4019 | 669 | 0.4 | 0.048509 |  | 1.457 |  | 1905 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04418316/WT | 17.5 | 72 | 16 | 7.1 | 5796 | 965 | 0.58 | 0.099752 |  | 1.462 |  | 2752 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04418321/FT | 17.5 | 72 | 21 | 9.1 | 5816 | 969 | 0.58 | 0.041742 |  | 1.467 |  | 2766 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04418321/WF | 17.5 | 72 | 21 | 9.1 | 4987 | 831 | 0.5 | 0.031414 |  | 1.472 |  | 2376 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04418321/WT | 17.5 | 72 | 21 | 9.1 | 7729 | 1287 | 0.77 | 0.071891 |  | 1.48 |  | 3692 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04420311/FT | 17.5 | 80 | 11 | 5.1 | 3564 | 535 | 0.36 | 0.032893 |  | 1.44 |  | 1680 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04420311/WF | 17.5 | 80 | 11 | 5.1 | 3048 | 458 | 0.3 | 0.023543 |  | 1.44 |  | 1437 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04420311/WT | 17.5 | 80 | 11 | 5.1 | 4365 | 655 | 0.44 | 0.047561 |  | 1.439 |  | 2057 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.04420316/FT | 17.5 | 80 | 16 | 7.1 | 5083 | 763 | 0.51 | 0.079675 |  | 1.455 |  | 2408 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04420316/WF | 17.5 | 80 | 16 | 7.1 | 4514 | 678 | 0.45 | 0.062539 |  | 1.457 |  | 2140 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04420316/WT | 17.5 | 80 | 16 | 7.1 | 6510 | 977 | 0.65 | 0.12747 |  | 1.462 |  | 3091 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.04420321/FT | 17.5 | 80 | 21 | 9.1 | 6533 | 981 | 0.65 | 0.053747 |  | 1.467 |  | 3107 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04420321/WF | 17.5 | 80 | 21 | 9.1 | 5603 | 841 | 0.56 | 0.040431 |  | 1.472 |  | 2669 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.04420321/WT | 17.5 | 80 | 21 | 9.1 | 8680 | 1303 | 0.87 | 0.0939 |  | 1.48 |  | 4146 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05906311/FF | 23 | 25 | 11 | 5.1 | 802 | 388 | 0.08 | 0.0010057 |  | 1.44 |  | 378 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05906311/FT | 23 | 25 | 11 | 5.1 | 1057 | 511 | 0.11 | 0.0018424 |  | 1.439 |  | 498 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05906311/WF | 23 | 25 | 11 | 5.1 | 972 | 470 | 0.1 | 0.0015368 |  | 1.438 |  | 458 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05906311/WT | 23 | 25 | 11 | 5.1 | 1217 | 589 | 0.12 | 0.0021744 |  | 1.437 |  | 573 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05906316/FF | 23 | 25 | 16 | 7.1 | 1099 | 532 | 0.11 | 0.0031826 |  | 1.457 |  | 521 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05906316/FT | 23 | 25 | 16 | 7.1 | 1542 | 746 | 0.15 | 0.0058661 |  | 1.462 |  | 732 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05906316/WF | 23 | 25 | 16 | 7.1 | 1397 | 676 | 0.14 | 0.0051197 |  | 1.464 |  | 664 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05906316/WT | 23 | 25 | 16 | 7.1 | 1843 | 892 | 0.18 | 0.0084062 |  | 1.468 |  | 877 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05906321/FF | 23 | 25 | 21 | 9.1 | 1385 | 670 | 0.14 | 0.0020133 |  | 1.472 |  | 660 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05906321/FT | 23 | 25 | 21 | 9.1 | 1985 | 960 | 0.2 | 0.0040483 |  | 1.48 |  | 948 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05906321/WF | 23 | 25 | 21 | 9.1 | 1815 | 878 | 0.18 | 0.0032931 |  | 1.484 |  | 868 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05906321/WT | 23 | 25 | 21 | 9.1 | 2431 | 1176 | 0.24 | 0.0057883 |  | 1.492 |  | 1166 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05908311/FF | 23 | 32.5 | 11 | 5.1 | 1182 | 434 | 0.12 | 0.0024951 |  | 1.44 |  | 557 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05908311/FT | 23 | 32.5 | 11 | 5.1 | 1553 | 570 | 0.16 | 0.004292 |  | 1.439 |  | 732 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05908311/WF | 23 | 32.5 | 11 | 5.1 | 1431 | 526 | 0.14 | 0.0033361 |  | 1.438 |  | 674 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05908311/WT | 23 | 32.5 | 11 | 5.1 | 1792 | 658 | 0.18 | 0.0053615 |  | 1.437 |  | 844 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05908316/FF | 23 | 32.5 | 16 | 7.1 | 1618 | 594 | 0.16 | 0.0069296 |  | 1.457 |  | 767 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05908316/FT | 23 | 32.5 | 16 | 7.1 | 2270 | 834 | 0.23 | 0.014139 |  | 1.462 |  | 1078 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05908316/WF | 23 | 32.5 | 16 | 7.1 | 2058 | 756 | 0.21 | 0.011823 |  | 1.464 |  | 978 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05908316/WT | 23 | 32.5 | 16 | 7.1 | 2711 | 996 | 0.27 | 0.019382 |  | 1.468 |  | 1290 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05908321/FF | 23 | 32.5 | 21 | 9.1 | 2038 | 748 | 0.2 | 0.0042866 |  | 1.472 |  | 971 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05908321/FT | 23 | 32.5 | 21 | 9.1 | 2921 | 1073 | 0.29 | 0.0088439 |  | 1.48 |  | 1395 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05908321/WF | 23 | 32.5 | 21 | 9.1 | 2670 | 981 | 0.27 | 0.0076931 |  | 1.484 |  | 1277 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05908321/WT | 23 | 32.5 | 21 | 9.1 | 3578 | 1314 | 0.36 | 0.013489 |  | 1.492 |  | 1716 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05910311/FF | 23 | 40.5 | 11 | 5.1 | 1559 | 461 | 0.16 | 0.0048204 |  | 1.44 |  | 735 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05910311/FT | 23 | 40.5 | 11 | 5.1 | 2052 | 607 | 0.21 | 0.0080231 |  | 1.439 |  | 967 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05910311/WF | 23 | 40.5 | 11 | 5.1 | 1889 | 559 | 0.19 | 0.0066503 |  | 1.438 |  | 890 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05910311/WT | 23 | 40.5 | 11 | 5.1 | 2366 | 700 | 0.24 | 0.010309 |  | 1.437 |  | 1114 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05910316/FF | 23 | 40.5 | 16 | 7.1 | 2137 | 632 | 0.21 | 0.01225 |  | 1.457 |  | 1013 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05910316/FT | 23 | 40.5 | 16 | 7.1 | 2997 | 887 | 0.3 | 0.024638 |  | 1.462 |  | 1423 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05910316/WF | 23 | 40.5 | 16 | 7.1 | 2717 | 804 | 0.27 | 0.02004 |  | 1.464 |  | 1291 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05910316/WT | 23 | 40.5 | 16 | 7.1 | 3582 | 1060 | 0.36 | 0.035232 |  | 1.468 |  | 1704 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05910321/FF | 23 | 40.5 | 21 | 9.1 | 2691 | 796 | 0.27 | 0.0080926 |  | 1.472 |  | 1282 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05910321/FT | 23 | 40.5 | 21 | 9.1 | 3856 | 1141 | 0.39 | 0.016526 |  | 1.48 |  | 1842 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05910321/WF | 23 | 40.5 | 21 | 9.1 | 3525 | 1043 | 0.35 | 0.013392 |  | 1.484 |  | 1686 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05910321/WT | 23 | 40.5 | 21 | 9.1 | 4727 | 1399 | 0.47 | 0.023756 |  | 1.492 |  | 2267 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05912311/FF | 23 | 48.5 | 11 | 5.1 | 1937 | 480 | 0.19 | 0.0073622 |  | 1.44 |  | 913 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05912311/FT | 23 | 48.5 | 11 | 5.1 | 2551 | 632 | 0.26 | 0.013208 |  | 1.439 |  | 1202 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05912311/WF | 23 | 48.5 | 11 | 5.1 | 2346 | 581 | 0.23 | 0.010508 |  | 1.438 |  | 1105 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05912311/WT | 23 | 48.5 | 11 | 5.1 | 2939 | 728 | 0.29 | 0.016195 |  | 1.437 |  | 1384 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05912316/FF | 23 | 48.5 | 16 | 7.1 | 2656 | 658 | 0.27 | 0.020698 |  | 1.457 |  | 1259 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05912316/FT | 23 | 48.5 | 16 | 7.1 | 3723 | 923 | 0.37 | 0.038311 |  | 1.462 |  | 1768 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05912316/WF | 23 | 48.5 | 16 | 7.1 | 3378 | 837 | 0.34 | 0.032473 |  | 1.464 |  | 1605 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05912316/WT | 23 | 48.5 | 16 | 7.1 | 4450 | 1103 | 0.45 | 0.05619 |  | 1.468 |  | 2117 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05912321/FF | 23 | 48.5 | 21 | 9.1 | 3344 | 829 | 0.33 | 0.01251 |  | 1.472 |  | 1593 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05912321/FT | 23 | 48.5 | 21 | 9.1 | 4792 | 1187 | 0.48 | 0.025826 |  | 1.48 |  | 2289 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05912321/WF | 23 | 48.5 | 21 | 9.1 | 4382 | 1086 | 0.44 | 0.021821 |  | 1.484 |  | 2096 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05912321/WT | 23 | 48.5 | 21 | 9.1 | 5874 | 1456 | 0.59 | 0.038526 |  | 1.492 |  | 2817 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05914311/FF | 23 | 56.5 | 11 | 5.1 | 2317 | 494 | 0.23 | 0.0115 |  | 1.44 |  | 1092 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05914311/FT | 23 | 56.5 | 11 | 5.1 | 3049 | 650 | 0.3 | 0.018826 |  | 1.439 |  | 1437 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05914311/WF | 23 | 56.5 | 11 | 5.1 | 2804 | 598 | 0.28 | 0.016563 |  | 1.438 |  | 1321 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05914311/WT | 23 | 56.5 | 11 | 5.1 | 3514 | 749 | 0.35 | 0.025073 |  | 1.437 |  | 1655 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05914316/FF | 23 | 56.5 | 16 | 7.1 | 3173 | 676 | 0.32 | 0.029726 |  | 1.457 |  | 1504 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05914316/FT | 23 | 56.5 | 16 | 7.1 | 4452 | 949 | 0.45 | 0.057778 |  | 1.462 |  | 2114 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05914316/WF | 23 | 56.5 | 16 | 7.1 | 4037 | 860 | 0.4 | 0.045918 |  | 1.464 |  | 1918 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05914316/WT | 23 | 56.5 | 16 | 7.1 | 5320 | 1134 | 0.53 | 0.079522 |  | 1.468 |  | 2531 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05914321/FF | 23 | 56.5 | 21 | 9.1 | 3997 | 852 | 0.4 | 0.018932 |  | 1.472 |  | 1904 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05914321/FT | 23 | 56.5 | 21 | 9.1 | 5728 | 1221 | 0.57 | 0.03748 |  | 1.48 |  | 2736 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05914321/WF | 23 | 56.5 | 21 | 9.1 | 5237 | 1116 | 0.52 | 0.031393 |  | 1.484 |  | 2505 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05914321/WT | 23 | 56.5 | 21 | 9.1 | 7021 | 1497 | 0.7 | 0.055747 |  | 1.492 |  | 3367 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05916311/FF | 23 | 64 | 11 | 5.1 | 2694 | 504 | 0.27 | 0.016791 |  | 1.44 |  | 1270 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05916311/FT | 23 | 64 | 11 | 5.1 | 3546 | 663 | 0.35 | 0.027127 |  | 1.439 |  | 1671 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05916311/WF | 23 | 64 | 11 | 5.1 | 3263 | 610 | 0.33 | 0.024329 |  | 1.438 |  | 1537 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05916311/WT | 23 | 64 | 11 | 5.1 | 4088 | 764 | 0.41 | 0.036364 |  | 1.437 |  | 1925 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05916316/FF | 23 | 64 | 16 | 7.1 | 3692 | 690 | 0.37 | 0.040576 |  | 1.457 |  | 1750 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05916316/FT | 23 | 64 | 16 | 7.1 | 5179 | 968 | 0.52 | 0.078654 |  | 1.462 |  | 2459 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05916316/WF | 23 | 64 | 16 | 7.1 | 4695 | 878 | 0.47 | 0.064605 |  | 1.464 |  | 2231 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05916316/WT | 23 | 64 | 16 | 7.1 | 6188 | 1157 | 0.62 | 0.1108 |  | 1.468 |  | 2944 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05916321/FF | 23 | 64 | 21 | 9.1 | 4652 | 870 | 0.47 | 0.026869 |  | 1.472 |  | 2216 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05916321/FT | 23 | 64 | 21 | 9.1 | 6664 | 1246 | 0.67 | 0.053131 |  | 1.48 |  | 3183 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05916321/WF | 23 | 64 | 21 | 9.1 | 6093 | 1139 | 0.61 | 0.044352 |  | 1.484 |  | 2914 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05916321/WT | 23 | 64 | 21 | 9.1 | 8168 | 1527 | 0.82 | 0.078422 |  | 1.492 |  | 3917 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05918311/FF | 23 | 72 | 11 | 5.1 | 3072 | 512 | 0.31 | 0.023337 |  | 1.44 |  | 1448 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05918311/FT | 23 | 72 | 11 | 5.1 | 4045 | 674 | 0.4 | 0.037327 |  | 1.439 |  | 1906 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05918311/WF | 23 | 72 | 11 | 5.1 | 3721 | 620 | 0.37 | 0.032328 |  | 1.438 |  | 1753 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05918311/WT | 23 | 72 | 11 | 5.1 | 4663 | 777 | 0.47 | 0.050272 |  | 1.437 |  | 2196 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05918316/FF | 23 | 72 | 16 | 7.1 | 4211 | 701 | 0.42 | 0.05332 |  | 1.457 |  | 1996 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05918316/FT | 23 | 72 | 16 | 7.1 | 5905 | 984 | 0.59 | 0.10312 |  | 1.462 |  | 2804 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05918316/WF | 23 | 72 | 16 | 7.1 | 5356 | 892 | 0.54 | 0.086825 |  | 1.464 |  | 2545 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05918316/WT | 23 | 72 | 16 | 7.1 | 7058 | 1176 | 0.71 | 0.14779 |  | 1.468 |  | 3358 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05918321/FF | 23 | 72 | 21 | 9.1 | 5304 | 883 | 0.53 | 0.035121 |  | 1.472 |  | 2527 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05918321/FT | 23 | 72 | 21 | 9.1 | 7600 | 1266 | 0.76 | 0.070108 |  | 1.48 |  | 3630 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05918321/WF | 23 | 72 | 21 | 9.1 | 6950 | 1158 | 0.7 | 0.059868 |  | 1.484 |  | 3324 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05918321/WT | 23 | 72 | 21 | 9.1 | 9315 | 1551 | 0.93 | 0.10334 |  | 1.492 |  | 4467 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05920311/FF | 23 | 80 | 11 | 5.1 | 3452 | 518 | 0.35 | 0.031235 |  | 1.44 |  | 1627 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05920311/FT | 23 | 80 | 11 | 5.1 | 4543 | 682 | 0.45 | 0.049568 |  | 1.439 |  | 2141 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05920311/WF | 23 | 80 | 11 | 5.1 | 4180 | 628 | 0.42 | 0.043661 |  | 1.438 |  | 1969 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05920311/WT | 23 | 80 | 11 | 5.1 | 5237 | 786 | 0.52 | 0.064683 |  | 1.437 |  | 2466 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.05920316/FF | 23 | 80 | 16 | 7.1 | 4730 | 710 | 0.47 | 0.068027 |  | 1.457 |  | 2242 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05920316/FT | 23 | 80 | 16 | 7.1 | 6634 | 996 | 0.66 | 0.1313 |  | 1.462 |  | 3150 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05920316/WF | 23 | 80 | 16 | 7.1 | 6015 | 903 | 0.6 | 0.10915 |  | 1.464 |  | 2858 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05920316/WT | 23 | 80 | 16 | 7.1 | 7926 | 1190 | 0.79 | 0.18611 |  | 1.468 |  | 3771 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.05920321/FF | 23 | 80 | 21 | 9.1 | 5957 | 894 | 0.6 | 0.046124 |  | 1.472 |  | 2838 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05920321/FT | 23 | 80 | 21 | 9.1 | 8538 | 1282 | 0.85 | 0.089807 |  | 1.48 |  | 4078 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05920321/WF | 23 | 80 | 21 | 9.1 | 7805 | 1172 | 0.78 | 0.076177 |  | 1.484 |  | 3733 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.05920321/WT | 23 | 80 | 21 | 9.1 | 10462 | 1571 | 1.05 | 0.13468 |  | 1.492 |  | 5017 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07406311/FF | 29 | 25 | 11 | 5.1 | 1010 | 489 | 0.1 | 0.0015368 |  | 1.438 |  | 476 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07406311/FT | 29 | 25 | 11 | 5.1 | 1261 | 610 | 0.13 | 0.0025326 |  | 1.437 |  | 594 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07406311/WF | 29 | 25 | 11 | 5.1 | 1208 | 584 | 0.12 | 0.0021744 |  | 1.437 |  | 569 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07406311/WT | 29 | 25 | 11 | 5.1 | 1340 | 648 | 0.13 | 0.0025326 |  | 1.436 |  | 631 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07406316/FF | 29 | 25 | 16 | 7.1 | 1389 | 672 | 0.14 | 0.0051197 |  | 1.464 |  | 660 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07406316/FT | 29 | 25 | 16 | 7.1 | 1860 | 900 | 0.19 | 0.009353 |  | 1.468 |  | 885 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07406316/WF | 29 | 25 | 16 | 7.1 | 1676 | 811 | 0.17 | 0.0075094 |  | 1.47 |  | 798 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07406316/WT | 29 | 25 | 16 | 7.1 | 2010 | 972 | 0.2 | 0.01035 |  | 1.474 |  | 958 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07406321/FF | 29 | 25 | 21 | 9.1 | 1737 | 840 | 0.17 | 0.0029443 |  | 1.484 |  | 831 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07406321/FT | 29 | 25 | 21 | 9.1 | 2252 | 1090 | 0.23 | 0.0053247 |  | 1.492 |  | 1080 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07406321/WF | 29 | 25 | 21 | 9.1 | 2066 | 1000 | 0.21 | 0.0044547 |  | 1.496 |  | 992 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07406321/WT | 29 | 25 | 21 | 9.1 | 2797 | 1353 | 0.28 | 0.0078333 |  | 1.505 |  | 1347 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07408311/FF | 29 | 32.5 | 11 | 5.1 | 1488 | 546 | 0.15 | 0.0037998 |  | 1.438 |  | 701 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07408311/FT | 29 | 32.5 | 11 | 5.1 | 1856 | 682 | 0.19 | 0.0059385 |  | 1.437 |  | 874 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07408311/WF | 29 | 32.5 | 11 | 5.1 | 1779 | 653 | 0.18 | 0.0053615 |  | 1.437 |  | 838 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07408311/WT | 29 | 32.5 | 11 | 5.1 | 1971 | 724 | 0.2 | 0.0065434 |  | 1.436 |  | 928 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07408316/FF | 29 | 32.5 | 16 | 7.1 | 2044 | 751 | 0.2 | 0.010742 |  | 1.464 |  | 971 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07408316/FT | 29 | 32.5 | 16 | 7.1 | 2737 | 1005 | 0.27 | 0.019382 |  | 1.468 |  | 1302 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07408316/WF | 29 | 32.5 | 16 | 7.1 | 2468 | 906 | 0.25 | 0.016659 |  | 1.47 |  | 1175 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07408316/WT | 29 | 32.5 | 16 | 7.1 | 2958 | 1086 | 0.3 | 0.023849 |  | 1.474 |  | 1410 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07408321/FF | 29 | 32.5 | 21 | 9.1 | 2555 | 938 | 0.26 | 0.0071472 |  | 1.484 |  | 1222 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07408321/FT | 29 | 32.5 | 21 | 9.1 | 3316 | 1218 | 0.33 | 0.011381 |  | 1.492 |  | 1590 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07408321/WF | 29 | 32.5 | 21 | 9.1 | 3043 | 1117 | 0.3 | 0.0094488 |  | 1.496 |  | 1461 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07408321/WT | 29 | 32.5 | 21 | 9.1 | 4115 | 1511 | 0.41 | 0.017393 |  | 1.505 |  | 1982 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07410311/FF | 29 | 40.5 | 11 | 5.1 | 1966 | 582 | 0.2 | 0.0073215 |  | 1.438 |  | 926 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07410311/FT | 29 | 40.5 | 11 | 5.1 | 2451 | 725 | 0.25 | 0.01113 |  | 1.437 |  | 1154 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07410311/WF | 29 | 40.5 | 11 | 5.1 | 2351 | 696 | 0.24 | 0.010309 |  | 1.437 |  | 1107 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07410311/WT | 29 | 40.5 | 11 | 5.1 | 2602 | 770 | 0.26 | 0.011982 |  | 1.436 |  | 1225 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07410316/FF | 29 | 40.5 | 16 | 7.1 | 2698 | 798 | 0.27 | 0.02004 |  | 1.464 |  | 1282 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07410316/FT | 29 | 40.5 | 16 | 7.1 | 3615 | 1070 | 0.36 | 0.035232 |  | 1.468 |  | 1720 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07410316/WF | 29 | 40.5 | 16 | 7.1 | 3260 | 965 | 0.33 | 0.029702 |  | 1.47 |  | 1552 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07410316/WT | 29 | 40.5 | 16 | 7.1 | 3906 | 1156 | 0.39 | 0.041226 |  | 1.474 |  | 1862 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07410321/FF | 29 | 40.5 | 21 | 9.1 | 3375 | 999 | 0.34 | 0.012658 |  | 1.484 |  | 1614 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07410321/FT | 29 | 40.5 | 21 | 9.1 | 4379 | 1296 | 0.44 | 0.020895 |  | 1.492 |  | 2100 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07410321/WF | 29 | 40.5 | 21 | 9.1 | 4017 | 1189 | 0.4 | 0.017359 |  | 1.496 |  | 1929 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07410321/WT | 29 | 40.5 | 21 | 9.1 | 5434 | 1608 | 0.54 | 0.031129 |  | 1.505 |  | 2617 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07412311/FF | 29 | 48.5 | 11 | 5.1 | 2441 | 605 | 0.24 | 0.011376 |  | 1.438 |  | 1150 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07412311/FT | 29 | 48.5 | 11 | 5.1 | 3045 | 755 | 0.3 | 0.017254 |  | 1.437 |  | 1434 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07412311/WF | 29 | 48.5 | 11 | 5.1 | 2920 | 724 | 0.29 | 0.016195 |  | 1.437 |  | 1375 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07412311/WT | 29 | 48.5 | 11 | 5.1 | 3235 | 802 | 0.32 | 0.019467 |  | 1.436 |  | 1523 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07412316/FF | 29 | 48.5 | 16 | 7.1 | 3355 | 831 | 0.34 | 0.032473 |  | 1.464 |  | 1594 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07412316/FT | 29 | 48.5 | 16 | 7.1 | 4492 | 1113 | 0.45 | 0.05619 |  | 1.468 |  | 2137 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07412316/WF | 29 | 48.5 | 16 | 7.1 | 4050 | 1004 | 0.41 | 0.046831 |  | 1.47 |  | 1928 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07412316/WT | 29 | 48.5 | 16 | 7.1 | 4854 | 1203 | 0.49 | 0.066386 |  | 1.474 |  | 2314 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07412321/FF | 29 | 48.5 | 21 | 9.1 | 4194 | 1039 | 0.42 | 0.019942 |  | 1.484 |  | 2006 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07412321/FT | 29 | 48.5 | 21 | 9.1 | 5441 | 1348 | 0.54 | 0.032447 |  | 1.492 |  | 2609 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07412321/WF | 29 | 48.5 | 21 | 9.1 | 4992 | 1237 | 0.5 | 0.027951 |  | 1.496 |  | 2397 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07412321/WT | 29 | 48.5 | 21 | 9.1 | 6754 | 1674 | 0.68 | 0.050748 |  | 1.505 |  | 3253 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07414311/FF | 29 | 56.5 | 11 | 5.1 | 2919 | 622 | 0.29 | 0.017678 |  | 1.438 |  | 1375 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07414311/FT | 29 | 56.5 | 11 | 5.1 | 3640 | 776 | 0.36 | 0.026422 |  | 1.437 |  | 1714 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07414311/WF | 29 | 56.5 | 11 | 5.1 | 3491 | 744 | 0.35 | 0.025073 |  | 1.437 |  | 1644 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07414311/WT | 29 | 56.5 | 11 | 5.1 | 3866 | 824 | 0.39 | 0.030667 |  | 1.436 |  | 1820 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07414316/FF | 29 | 56.5 | 16 | 7.1 | 4009 | 855 | 0.4 | 0.045918 |  | 1.464 |  | 1905 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07414316/FT | 29 | 56.5 | 16 | 7.1 | 5370 | 1145 | 0.54 | 0.082478 |  | 1.468 |  | 2555 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07414316/WF | 29 | 56.5 | 16 | 7.1 | 4842 | 1032 | 0.48 | 0.065533 |  | 1.47 |  | 2305 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07414316/WT | 29 | 56.5 | 16 | 7.1 | 5802 | 1237 | 0.58 | 0.094835 |  | 1.474 |  | 2766 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07414321/FF | 29 | 56.5 | 21 | 9.1 | 5014 | 1069 | 0.5 | 0.029105 |  | 1.484 |  | 2398 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07414321/FT | 29 | 56.5 | 21 | 9.1 | 6504 | 1386 | 0.65 | 0.048306 |  | 1.492 |  | 3119 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07414321/WF | 29 | 56.5 | 21 | 9.1 | 5966 | 1272 | 0.6 | 0.041383 |  | 1.496 |  | 2865 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07414321/WT | 29 | 56.5 | 21 | 9.1 | 8073 | 1721 | 0.81 | 0.073939 |  | 1.505 |  | 3888 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07416311/FF | 29 | 64 | 11 | 5.1 | 3396 | 635 | 0.34 | 0.02571 |  | 1.438 |  | 1600 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07416311/FT | 29 | 64 | 11 | 5.1 | 4234 | 792 | 0.42 | 0.038025 |  | 1.437 |  | 1994 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07416311/WF | 29 | 64 | 11 | 5.1 | 4062 | 760 | 0.41 | 0.036364 |  | 1.437 |  | 1913 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07416311/WT | 29 | 64 | 11 | 5.1 | 4499 | 841 | 0.45 | 0.043215 |  | 1.436 |  | 2118 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07416316/FF | 29 | 64 | 16 | 7.1 | 4664 | 872 | 0.47 | 0.064605 |  | 1.464 |  | 2216 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07416316/FT | 29 | 64 | 16 | 7.1 | 6247 | 1168 | 0.62 | 0.1108 |  | 1.468 |  | 2972 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07416316/WF | 29 | 64 | 16 | 7.1 | 5631 | 1053 | 0.56 | 0.090865 |  | 1.47 |  | 2681 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07416316/WT | 29 | 64 | 16 | 7.1 | 6750 | 1262 | 0.68 | 0.13266 |  | 1.474 |  | 3218 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07416321/FF | 29 | 64 | 21 | 9.1 | 5833 | 1091 | 0.58 | 0.040251 |  | 1.484 |  | 2790 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07416321/FT | 29 | 64 | 21 | 9.1 | 7565 | 1415 | 0.76 | 0.067734 |  | 1.492 |  | 3628 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07416321/WF | 29 | 64 | 21 | 9.1 | 6941 | 1298 | 0.69 | 0.056227 |  | 1.496 |  | 3333 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07416321/WT | 29 | 64 | 21 | 9.1 | 9391 | 1756 | 0.94 | 0.10207 |  | 1.505 |  | 4523 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07418311/FF | 29 | 72 | 11 | 5.1 | 3872 | 645 | 0.39 | 0.035624 |  | 1.438 |  | 1824 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07418311/FT | 29 | 72 | 11 | 5.1 | 4831 | 805 | 0.48 | 0.052266 |  | 1.437 |  | 2275 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07418311/WF | 29 | 72 | 11 | 5.1 | 4631 | 771 | 0.46 | 0.048313 |  | 1.437 |  | 2181 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07418311/WT | 29 | 72 | 11 | 5.1 | 5130 | 854 | 0.51 | 0.058464 |  | 1.436 |  | 2415 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07418316/FF | 29 | 72 | 16 | 7.1 | 5318 | 886 | 0.53 | 0.083731 |  | 1.464 |  | 2527 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07418316/FT | 29 | 72 | 16 | 7.1 | 7125 | 1187 | 0.71 | 0.14779 |  | 1.468 |  | 3390 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07418316/WF | 29 | 72 | 16 | 7.1 | 6423 | 1070 | 0.64 | 0.12078 |  | 1.47 |  | 3058 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07418316/WT | 29 | 72 | 16 | 7.1 | 7697 | 1282 | 0.77 | 0.17306 |  | 1.474 |  | 3669 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07418321/FF | 29 | 72 | 21 | 9.1 | 6653 | 1108 | 0.67 | 0.055042 |  | 1.484 |  | 3182 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07418321/FT | 29 | 72 | 21 | 9.1 | 8629 | 1437 | 0.86 | 0.088905 |  | 1.492 |  | 4138 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07418321/WF | 29 | 72 | 21 | 9.1 | 7916 | 1318 | 0.79 | 0.075521 |  | 1.496 |  | 3801 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07418321/WT | 29 | 72 | 21 | 9.1 | 10710 | 1784 | 1.07 | 0.13537 |  | 1.505 |  | 5158 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07420311/FF | 29 | 80 | 11 | 5.1 | 4350 | 653 | 0.44 | 0.047561 |  | 1.438 |  | 2049 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07420311/FT | 29 | 80 | 11 | 5.1 | 5426 | 815 | 0.54 | 0.06934 |  | 1.437 |  | 2555 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07420311/WF | 29 | 80 | 11 | 5.1 | 5203 | 781 | 0.52 | 0.064683 |  | 1.437 |  | 2450 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07420311/WT | 29 | 80 | 11 | 5.1 | 5763 | 865 | 0.58 | 0.079103 |  | 1.436 |  | 2713 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Maxi | MAXW.07420316/FF | 29 | 80 | 16 | 7.1 | 5973 | 897 | 0.6 | 0.10915 |  | 1.464 |  | 2838 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07420316/FT | 29 | 80 | 16 | 7.1 | 8002 | 1201 | 0.8 | 0.19071 |  | 1.468 |  | 3807 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07420316/WF | 29 | 80 | 16 | 7.1 | 7215 | 1083 | 0.72 | 0.15544 |  | 1.47 |  | 3435 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07420316/WT | 29 | 80 | 16 | 7.1 | 8645 | 1298 | 0.86 | 0.21947 |  | 1.474 |  | 4121 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Maxi | MAXW.07420321/FF | 29 | 80 | 21 | 9.1 | 7470 | 1122 | 0.75 | 0.070668 |  | 1.484 |  | 3573 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07420321/FT | 29 | 80 | 21 | 9.1 | 9692 | 1455 | 0.97 | 0.11568 |  | 1.492 |  | 4648 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07420321/WF | 29 | 80 | 21 | 9.1 | 8892 | 1335 | 0.89 | 0.09808 |  | 1.496 |  | 4270 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Maxi | MAXW.07420321/WT | 29 | 80 | 21 | 9.1 | 12030 | 1806 | 1.2 | 0.17405 |  | 1.505 |  | 5794 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Build-In Floor | Mini Canal | MICL.00907014/DNA | 3.5 | 27.5 | DNA | 5.5 | 161 | 70 | 0.02 | 3.6531e-05 |  | 1.362 |  | 74 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00907018/DNA | 3.5 | 27.5 | DNA | 7.1 | 189 | 82 | 0.02 | 7.1997e-05 |  | 1.362 |  | 87 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00907026/DNA | 3.5 | 27.5 | DNA | 10.2 | 250 | 109 | 0.03 | 0.00015429 |  | 1.362 |  | 115 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00907034/DNA | 3.5 | 27.5 | DNA | 13.4 | 324 | 141 | 0.03 | 0.0004442 |  | 1.362 |  | 149 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00907042/DNA | 3.5 | 27.5 | DNA | 16.5 | 468 | 204 | 0.05 | 0.00023499 |  | 1.362 |  | 215 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00908014/DNA | 3.5 | 31.5 | DNA | 5.5 | 200 | 76 | 0.02 | 3.9991e-05 |  | 1.362 |  | 92 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00908018/DNA | 3.5 | 31.5 | DNA | 7.1 | 239 | 91 | 0.02 | 8.1193e-05 |  | 1.362 |  | 110 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00908026/DNA | 3.5 | 31.5 | DNA | 10.2 | 313 | 119 | 0.03 | 0.00017329 |  | 1.362 |  | 144 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00908034/DNA | 3.5 | 31.5 | DNA | 13.4 | 407 | 155 | 0.04 | 0.00080835 |  | 1.362 |  | 187 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00908042/DNA | 3.5 | 31.5 | DNA | 16.5 | 588 | 224 | 0.06 | 0.00035704 |  | 1.362 |  | 270 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00909014/DNA | 3.5 | 35.5 | DNA | 5.5 | 242 | 82 | 0.02 | 4.3451e-05 |  | 1.362 |  | 111 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00909018/DNA | 3.5 | 35.5 | DNA | 7.1 | 285 | 97 | 0.03 | 0.00019229 |  | 1.362 |  | 131 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00909026/DNA | 3.5 | 35.5 | DNA | 10.2 | 377 | 128 | 0.04 | 0.00032885 |  | 1.362 |  | 173 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00909034/DNA | 3.5 | 35.5 | DNA | 13.4 | 488 | 165 | 0.05 | 0.0012968 |  | 1.362 |  | 224 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00909042/DNA | 3.5 | 35.5 | DNA | 16.5 | 703 | 238 | 0.07 | 0.00051015 |  | 1.362 |  | 323 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00910014/DNA | 3.5 | 39.5 | DNA | 5.5 | 281 | 86 | 0.03 | 0.00010297 |  | 1.362 |  | 129 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00910018/DNA | 3.5 | 39.5 | DNA | 7.1 | 333 | 101 | 0.03 | 0.00021129 |  | 1.362 |  | 153 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00910026/DNA | 3.5 | 39.5 | DNA | 10.2 | 438 | 134 | 0.04 | 0.00036064 |  | 1.362 |  | 201 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00910034/DNA | 3.5 | 39.5 | DNA | 13.4 | 568 | 173 | 0.06 | 0.0019177 |  | 1.362 |  | 261 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00910042/DNA | 3.5 | 39.5 | DNA | 16.5 | 818 | 249 | 0.08 | 0.00069662 |  | 1.362 |  | 376 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00911014/DNA | 3.5 | 43.5 | DNA | 5.5 | 320 | 89 | 0.03 | 0.00011042 |  | 1.362 |  | 147 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00911018/DNA | 3.5 | 43.5 | DNA | 7.1 | 381 | 106 | 0.04 | 0.00039244 |  | 1.362 |  | 175 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00911026/DNA | 3.5 | 43.5 | DNA | 10.2 | 501 | 139 | 0.05 | 0.0005937 |  | 1.362 |  | 230 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00911034/DNA | 3.5 | 43.5 | DNA | 13.4 | 649 | 180 | 0.06 | 0.0020974 |  | 1.362 |  | 298 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00911042/DNA | 3.5 | 43.5 | DNA | 16.5 | 940 | 260 | 0.09 | 0.00091866 |  | 1.362 |  | 432 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00912014/DNA | 3.5 | 47 | DNA | 5.5 | 364 | 92 | 0.04 | 0.00020557 |  | 1.362 |  | 167 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00912018/DNA | 3.5 | 47 | DNA | 7.1 | 429 | 109 | 0.04 | 0.00042424 |  | 1.362 |  | 197 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00912026/DNA | 3.5 | 47 | DNA | 10.2 | 564 | 143 | 0.06 | 0.00089867 |  | 1.362 |  | 259 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00912034/DNA | 3.5 | 47 | DNA | 13.4 | 731 | 186 | 0.07 | 0.0029023 |  | 1.362 |  | 336 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00912042/DNA | 3.5 | 47 | DNA | 16.5 | 1056 | 268 | 0.11 | 0.001409 |  | 1.362 |  | 485 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00913014/DNA | 3.5 | 51 | DNA | 5.5 | 401 | 94 | 0.04 | 0.00021839 |  | 1.362 |  | 184 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00913018/DNA | 3.5 | 51 | DNA | 7.1 | 475 | 111 | 0.05 | 0.00068852 |  | 1.362 |  | 218 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00913026/DNA | 3.5 | 51 | DNA | 10.2 | 625 | 147 | 0.06 | 0.00096437 |  | 1.362 |  | 287 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00913034/DNA | 3.5 | 51 | DNA | 13.4 | 812 | 190 | 0.08 | 0.0038564 |  | 1.362 |  | 373 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00913042/DNA | 3.5 | 51 | DNA | 16.5 | 1171 | 275 | 0.12 | 0.0017391 |  | 1.362 |  | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00915014/DNA | 3.5 | 59 | DNA | 5.5 | 483 | 98 | 0.05 | 0.00037517 |  | 1.362 |  | 222 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00915018/DNA | 3.5 | 59 | DNA | 7.1 | 572 | 116 | 0.06 | 0.0010958 |  | 1.362 |  | 263 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00915026/DNA | 3.5 | 59 | DNA | 10.2 | 751 | 153 | 0.08 | 0.001862 |  | 1.362 |  | 345 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00915034/DNA | 3.5 | 59 | DNA | 13.4 | 975 | 198 | 0.1 | 0.0062358 |  | 1.362 |  | 448 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00915042/DNA | 3.5 | 59 | DNA | 16.5 | 1406 | 286 | 0.14 | 0.0025304 |  | 1.362 |  | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00917014/DNA | 3.5 | 67 | DNA | 5.5 | 564 | 101 | 0.06 | 0.00058836 |  | 1.362 |  | 259 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00917018/DNA | 3.5 | 67 | DNA | 7.1 | 668 | 120 | 0.07 | 0.0016288 |  | 1.362 |  | 307 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00917026/DNA | 3.5 | 67 | DNA | 10.2 | 877 | 157 | 0.09 | 0.0025853 |  | 1.362 |  | 403 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00917034/DNA | 3.5 | 67 | DNA | 13.4 | 1136 | 204 | 0.11 | 0.0080995 |  | 1.362 |  | 522 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00917042/DNA | 3.5 | 67 | DNA | 16.5 | 1643 | 295 | 0.16 | 0.0035094 |  | 1.362 |  | 755 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00919014/DNA | 3.5 | 75 | DNA | 5.5 | 642 | 103 | 0.06 | 0.00064352 |  | 1.362 |  | 295 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00919018/DNA | 3.5 | 75 | DNA | 7.1 | 760 | 122 | 0.08 | 0.0023018 |  | 1.362 |  | 349 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00919026/DNA | 3.5 | 75 | DNA | 10.2 | 1001 | 161 | 0.1 | 0.0034662 |  | 1.362 |  | 460 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00919034/DNA | 3.5 | 75 | DNA | 13.4 | 1299 | 208 | 0.13 | 0.011606 |  | 1.362 |  | 597 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00919042/DNA | 3.5 | 75 | DNA | 16.5 | 1874 | 301 | 0.19 | 0.0051838 |  | 1.362 |  | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00921014/DNA | 3.5 | 82.5 | DNA | 5.5 | 723 | 105 | 0.07 | 0.00093922 |  | 1.362 |  | 332 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00921018/DNA | 3.5 | 82.5 | DNA | 7.1 | 858 | 125 | 0.09 | 0.0031283 |  | 1.362 |  | 394 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00921026/DNA | 3.5 | 82.5 | DNA | 10.2 | 1128 | 164 | 0.11 | 0.0045177 |  | 1.362 |  | 518 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00921034/DNA | 3.5 | 82.5 | DNA | 13.4 | 1461 | 212 | 0.15 | 0.015844 |  | 1.362 |  | 671 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00921042/DNA | 3.5 | 82.5 | DNA | 16.5 | 2111 | 306 | 0.21 | 0.0066616 |  | 1.362 |  | 970 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00923014/DNA | 3.5 | 90.5 | DNA | 5.5 | 805 | 107 | 0.08 | 0.0013086 |  | 1.362 |  | 370 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00923018/DNA | 3.5 | 90.5 | DNA | 7.1 | 951 | 126 | 0.1 | 0.0041219 |  | 1.362 |  | 437 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00923026/DNA | 3.5 | 90.5 | DNA | 10.2 | 1252 | 166 | 0.13 | 0.0066604 |  | 1.362 |  | 575 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00923034/DNA | 3.5 | 90.5 | DNA | 13.4 | 1624 | 215 | 0.16 | 0.018978 |  | 1.362 |  | 746 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00923042/DNA | 3.5 | 90.5 | DNA | 16.5 | 2346 | 311 | 0.23 | 0.0083743 |  | 1.362 |  | 1078 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00925014/DNA | 3.5 | 98.5 | DNA | 5.5 | 884 | 108 | 0.09 | 0.0017589 |  | 1.362 |  | 406 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00925018/DNA | 3.5 | 98.5 | DNA | 7.1 | 1047 | 128 | 0.1 | 0.0044497 |  | 1.362 |  | 481 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00925026/DNA | 3.5 | 98.5 | DNA | 10.2 | 1376 | 168 | 0.14 | 0.0082266 |  | 1.362 |  | 632 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00925034/DNA | 3.5 | 98.5 | DNA | 13.4 | 1787 | 218 | 0.18 | 0.02451 |  | 1.362 |  | 821 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00925042/DNA | 3.5 | 98.5 | DNA | 16.5 | 2577 | 314 | 0.26 | 0.011106 |  | 1.362 |  | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00927014/DNA | 3.5 | 106.5 | DNA | 5.5 | 964 | 109 | 0.1 | 0.0022972 |  | 1.362 |  | 443 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00927018/DNA | 3.5 | 106.5 | DNA | 7.1 | 1143 | 129 | 0.11 | 0.0056842 |  | 1.362 |  | 525 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00927026/DNA | 3.5 | 106.5 | DNA | 10.2 | 1502 | 170 | 0.15 | 0.01001 |  | 1.362 |  | 690 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00927034/DNA | 3.5 | 106.5 | DNA | 13.4 | 1948 | 220 | 0.19 | 0.028514 |  | 1.362 |  | 895 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00927042/DNA | 3.5 | 106.5 | DNA | 16.5 | 2814 | 318 | 0.28 | 0.013422 |  | 1.362 |  | 1293 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00929014/DNA | 3.5 | 114 | DNA | 5.5 | 1045 | 110 | 0.1 | 0.002442 |  | 1.362 |  | 480 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00929018/DNA | 3.5 | 114 | DNA | 7.1 | 1236 | 130 | 0.12 | 0.0071161 |  | 1.362 |  | 568 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00929026/DNA | 3.5 | 114 | DNA | 10.2 | 1628 | 171 | 0.16 | 0.012022 |  | 1.362 |  | 748 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00929034/DNA | 3.5 | 114 | DNA | 13.4 | 2111 | 222 | 0.21 | 0.03543 |  | 1.362 |  | 970 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00929042/DNA | 3.5 | 114 | DNA | 16.5 | 3050 | 321 | 0.31 | 0.017004 |  | 1.362 |  | 1401 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00931014/DNA | 3.5 | 122 | DNA | 5.5 | 1125 | 111 | 0.11 | 0.0031039 |  | 1.362 |  | 517 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00931018/DNA | 3.5 | 122 | DNA | 7.1 | 1332 | 131 | 0.13 | 0.0087577 |  | 1.362 |  | 612 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00931026/DNA | 3.5 | 122 | DNA | 10.2 | 1752 | 172 | 0.18 | 0.015841 |  | 1.362 |  | 805 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00931034/DNA | 3.5 | 122 | DNA | 13.4 | 2272 | 223 | 0.23 | 0.043214 |  | 1.362 |  | 1044 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00931042/DNA | 3.5 | 122 | DNA | 16.5 | 3282 | 323 | 0.33 | 0.01999 |  | 1.362 |  | 1508 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00933014/DNA | 3.5 | 130 | DNA | 5.5 | 1206 | 111 | 0.12 | 0.00387 |  | 1.362 |  | 554 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00933018/DNA | 3.5 | 130 | DNA | 7.1 | 1428 | 132 | 0.14 | 0.010621 |  | 1.362 |  | 656 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00933026/DNA | 3.5 | 130 | DNA | 10.2 | 1876 | 173 | 0.19 | 0.018515 |  | 1.362 |  | 862 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00933034/DNA | 3.5 | 130 | DNA | 13.4 | 2436 | 225 | 0.24 | 0.048743 |  | 1.362 |  | 1119 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00933042/DNA | 3.5 | 130 | DNA | 16.5 | 3518 | 325 | 0.35 | 0.023283 |  | 1.362 |  | 1616 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00935014/DNA | 3.5 | 138 | DNA | 5.5 | 1286 | 112 | 0.13 | 0.0047474 |  | 1.362 |  | 591 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00935018/DNA | 3.5 | 138 | DNA | 7.1 | 1524 | 133 | 0.15 | 0.012719 |  | 1.362 |  | 700 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00935026/DNA | 3.5 | 138 | DNA | 10.2 | 2003 | 174 | 0.2 | 0.021462 |  | 1.362 |  | 920 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00935034/DNA | 3.5 | 138 | DNA | 13.4 | 2599 | 226 | 0.26 | 0.058037 |  | 1.362 |  | 1194 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00935042/DNA | 3.5 | 138 | DNA | 16.5 | 3753 | 327 | 0.38 | 0.02823 |  | 1.362 |  | 1724 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00937014/DNA | 3.5 | 145.5 | DNA | 5.5 | 1367 | 113 | 0.14 | 0.0057427 |  | 1.362 |  | 628 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00937018/DNA | 3.5 | 145.5 | DNA | 7.1 | 1619 | 133 | 0.16 | 0.015063 |  | 1.362 |  | 744 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00937026/DNA | 3.5 | 145.5 | DNA | 10.2 | 2129 | 175 | 0.21 | 0.024691 |  | 1.362 |  | 978 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00937034/DNA | 3.5 | 145.5 | DNA | 13.4 | 2760 | 227 | 0.28 | 0.068269 |  | 1.362 |  | 1268 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00937042/DNA | 3.5 | 145.5 | DNA | 16.5 | 3986 | 328 | 0.4 | 0.032286 |  | 1.362 |  | 1831 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00939014/DNA | 3.5 | 153.5 | DNA | 5.5 | 1445 | 113 | 0.14 | 0.0060162 |  | 1.362 |  | 664 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00939018/DNA | 3.5 | 153.5 | DNA | 7.1 | 1713 | 134 | 0.17 | 0.017664 |  | 1.362 |  | 787 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00939026/DNA | 3.5 | 153.5 | DNA | 10.2 | 2253 | 176 | 0.23 | 0.030588 |  | 1.362 |  | 1035 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00939034/DNA | 3.5 | 153.5 | DNA | 13.4 | 2923 | 228 | 0.29 | 0.075452 |  | 1.362 |  | 1343 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00939042/DNA | 3.5 | 153.5 | DNA | 16.5 | 4221 | 330 | 0.42 | 0.036687 |  | 1.362 |  | 1939 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00941014/DNA | 3.5 | 161.5 | DNA | 5.5 | 1526 | 113 | 0.15 | 0.0071743 |  | 1.362 |  | 701 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00941018/DNA | 3.5 | 161.5 | DNA | 7.1 | 1807 | 134 | 0.18 | 0.020535 |  | 1.362 |  | 830 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00941026/DNA | 3.5 | 161.5 | DNA | 10.2 | 2377 | 177 | 0.24 | 0.034619 |  | 1.362 |  | 1092 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00941034/DNA | 3.5 | 161.5 | DNA | 13.4 | 3084 | 229 | 0.31 | 0.087306 |  | 1.362 |  | 1417 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00941042/DNA | 3.5 | 161.5 | DNA | 16.5 | 4458 | 331 | 0.45 | 0.043167 |  | 1.362 |  | 2048 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00943014/DNA | 3.5 | 169.5 | DNA | 5.5 | 1606 | 114 | 0.16 | 0.0084662 |  | 1.362 |  | 738 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00943018/DNA | 3.5 | 169.5 | DNA | 7.1 | 1905 | 135 | 0.19 | 0.023686 |  | 1.362 |  | 875 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00943026/DNA | 3.5 | 169.5 | DNA | 10.2 | 2503 | 177 | 0.25 | 0.038973 |  | 1.362 |  | 1150 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00943034/DNA | 3.5 | 169.5 | DNA | 13.4 | 3248 | 230 | 0.32 | 0.095572 |  | 1.362 |  | 1492 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00943042/DNA | 3.5 | 169.5 | DNA | 16.5 | 4689 | 332 | 0.47 | 0.048418 |  | 1.362 |  | 2154 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00945014/DNA | 3.5 | 177 | DNA | 5.5 | 1689 | 114 | 0.17 | 0.0098984 |  | 1.362 |  | 776 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00945018/DNA | 3.5 | 177 | DNA | 7.1 | 2000 | 135 | 0.2 | 0.02713 |  | 1.362 |  | 919 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00945026/DNA | 3.5 | 177 | DNA | 10.2 | 2629 | 178 | 0.26 | 0.043662 |  | 1.362 |  | 1208 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00945034/DNA | 3.5 | 177 | DNA | 13.4 | 3411 | 231 | 0.34 | 0.10911 |  | 1.362 |  | 1567 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00945042/DNA | 3.5 | 177 | DNA | 16.5 | 4924 | 334 | 0.49 | 0.054052 |  | 1.362 |  | 2262 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00947014/DNA | 3.5 | 185 | DNA | 5.5 | 1770 | 115 | 0.18 | 0.011478 |  | 1.362 |  | 813 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00947018/DNA | 3.5 | 185 | DNA | 7.1 | 2094 | 136 | 0.21 | 0.030876 |  | 1.362 |  | 962 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00947026/DNA | 3.5 | 185 | DNA | 10.2 | 2754 | 179 | 0.28 | 0.052017 |  | 1.362 |  | 1265 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00947034/DNA | 3.5 | 185 | DNA | 13.4 | 3572 | 232 | 0.36 | 0.12369 |  | 1.362 |  | 1641 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00947042/DNA | 3.5 | 185 | DNA | 16.5 | 5161 | 335 | 0.52 | 0.062224 |  | 1.362 |  | 2371 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.00949014/DNA | 3.5 | 193 | DNA | 5.5 | 1848 | 115 | 0.18 | 0.011917 |  | 1.362 |  | 849 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.00949018/DNA | 3.5 | 193 | DNA | 7.1 | 2190 | 136 | 0.22 | 0.034937 |  | 1.362 |  | 1006 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00949026/DNA | 3.5 | 193 | DNA | 10.2 | 2878 | 179 | 0.29 | 0.057639 |  | 1.362 |  | 1322 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.00949034/DNA | 3.5 | 193 | DNA | 13.4 | 3735 | 232 | 0.37 | 0.13379 |  | 1.362 |  | 1716 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.00949042/DNA | 3.5 | 193 | DNA | 16.5 | 5394 | 336 | 0.54 | 0.068793 |  | 1.362 |  | 2478 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01107014/DNA | 4.5 | 27.5 | DNA | 5.5 | 183 | 80 | 0.02 | 3.6531e-05 |  | 1.362 |  | 84 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01107018/DNA | 4.5 | 27.5 | DNA | 7.1 | 220 | 96 | 0.02 | 7.1997e-05 |  | 1.362 |  | 101 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01107026/DNA | 4.5 | 27.5 | DNA | 10.2 | 296 | 129 | 0.03 | 0.00015429 |  | 1.362 |  | 136 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01107034/DNA | 4.5 | 27.5 | DNA | 13.4 | 385 | 168 | 0.04 | 0.00070766 |  | 1.362 |  | 177 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01107042/DNA | 4.5 | 27.5 | DNA | 16.5 | 538 | 234 | 0.05 | 0.00023499 |  | 1.362 |  | 247 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01108014/DNA | 4.5 | 31.5 | DNA | 5.5 | 231 | 88 | 0.02 | 3.9991e-05 |  | 1.362 |  | 106 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01108018/DNA | 4.5 | 31.5 | DNA | 7.1 | 272 | 104 | 0.03 | 0.00017329 |  | 1.362 |  | 125 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01108026/DNA | 4.5 | 31.5 | DNA | 10.2 | 370 | 141 | 0.04 | 0.00029705 |  | 1.362 |  | 170 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01108034/DNA | 4.5 | 31.5 | DNA | 13.4 | 479 | 182 | 0.05 | 0.0011583 |  | 1.362 |  | 220 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01108042/DNA | 4.5 | 31.5 | DNA | 16.5 | 673 | 256 | 0.07 | 0.00047866 |  | 1.362 |  | 309 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01109014/DNA | 4.5 | 35.5 | DNA | 5.5 | 276 | 93 | 0.03 | 9.5527e-05 |  | 1.362 |  | 127 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01109018/DNA | 4.5 | 35.5 | DNA | 7.1 | 327 | 111 | 0.03 | 0.00019229 |  | 1.362 |  | 150 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01109026/DNA | 4.5 | 35.5 | DNA | 10.2 | 444 | 150 | 0.04 | 0.00032885 |  | 1.362 |  | 204 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01109034/DNA | 4.5 | 35.5 | DNA | 13.4 | 575 | 195 | 0.06 | 0.001738 |  | 1.362 |  | 264 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01109042/DNA | 4.5 | 35.5 | DNA | 16.5 | 810 | 274 | 0.08 | 0.00065692 |  | 1.362 |  | 372 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01110014/DNA | 4.5 | 39.5 | DNA | 5.5 | 322 | 98 | 0.03 | 0.00010297 |  | 1.362 |  | 148 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01110018/DNA | 4.5 | 39.5 | DNA | 7.1 | 383 | 117 | 0.04 | 0.00036064 |  | 1.362 |  | 176 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01110026/DNA | 4.5 | 39.5 | DNA | 10.2 | 518 | 158 | 0.05 | 0.0005463 |  | 1.362 |  | 238 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01110034/DNA | 4.5 | 39.5 | DNA | 13.4 | 668 | 204 | 0.07 | 0.0024543 |  | 1.362 |  | 307 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01110042/DNA | 4.5 | 39.5 | DNA | 16.5 | 945 | 288 | 0.09 | 0.00086997 |  | 1.362 |  | 434 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01111014/DNA | 4.5 | 43.5 | DNA | 5.5 | 370 | 103 | 0.04 | 0.00019275 |  | 1.362 |  | 170 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01111018/DNA | 4.5 | 43.5 | DNA | 7.1 | 438 | 121 | 0.04 | 0.00039244 |  | 1.362 |  | 201 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01111026/DNA | 4.5 | 43.5 | DNA | 10.2 | 590 | 163 | 0.06 | 0.00083297 |  | 1.362 |  | 271 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01111034/DNA | 4.5 | 43.5 | DNA | 13.4 | 766 | 212 | 0.08 | 0.0033143 |  | 1.362 |  | 352 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01111042/DNA | 4.5 | 43.5 | DNA | 16.5 | 1077 | 298 | 0.11 | 0.00134 |  | 1.362 |  | 495 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01112014/DNA | 4.5 | 47 | DNA | 5.5 | 416 | 106 | 0.04 | 0.00020557 |  | 1.362 |  | 191 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01112018/DNA | 4.5 | 47 | DNA | 7.1 | 492 | 125 | 0.05 | 0.00064111 |  | 1.362 |  | 226 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01112026/DNA | 4.5 | 47 | DNA | 10.2 | 664 | 169 | 0.07 | 0.0011959 |  | 1.362 |  | 305 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01112034/DNA | 4.5 | 47 | DNA | 13.4 | 864 | 219 | 0.09 | 0.0043242 |  | 1.362 |  | 397 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01112042/DNA | 4.5 | 47 | DNA | 16.5 | 1212 | 308 | 0.12 | 0.0016589 |  | 1.362 |  | 557 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01113014/DNA | 4.5 | 51 | DNA | 5.5 | 459 | 108 | 0.05 | 0.00033608 |  | 1.362 |  | 211 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01113018/DNA | 4.5 | 51 | DNA | 7.1 | 546 | 128 | 0.05 | 0.00068852 |  | 1.362 |  | 251 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01113026/DNA | 4.5 | 51 | DNA | 10.2 | 738 | 173 | 0.07 | 0.0012825 |  | 1.362 |  | 339 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01113034/DNA | 4.5 | 51 | DNA | 13.4 | 958 | 225 | 0.1 | 0.0054902 |  | 1.362 |  | 440 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01113042/DNA | 4.5 | 51 | DNA | 16.5 | 1347 | 316 | 0.13 | 0.0020201 |  | 1.362 |  | 619 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01115014/DNA | 4.5 | 59 | DNA | 5.5 | 553 | 112 | 0.06 | 0.00053319 |  | 1.362 |  | 254 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01115018/DNA | 4.5 | 59 | DNA | 7.1 | 655 | 133 | 0.07 | 0.0014557 |  | 1.362 |  | 301 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01115026/DNA | 4.5 | 59 | DNA | 10.2 | 886 | 180 | 0.09 | 0.0023138 |  | 1.362 |  | 407 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01115034/DNA | 4.5 | 59 | DNA | 13.4 | 1149 | 233 | 0.11 | 0.0072451 |  | 1.362 |  | 528 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01115042/DNA | 4.5 | 59 | DNA | 16.5 | 1617 | 329 | 0.16 | 0.0032452 |  | 1.362 |  | 743 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01117014/DNA | 4.5 | 67 | DNA | 5.5 | 646 | 116 | 0.06 | 0.00058836 |  | 1.362 |  | 297 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01117018/DNA | 4.5 | 67 | DNA | 7.1 | 766 | 137 | 0.08 | 0.0020819 |  | 1.362 |  | 352 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01117026/DNA | 4.5 | 67 | DNA | 10.2 | 1032 | 185 | 0.1 | 0.0031383 |  | 1.362 |  | 474 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01117034/DNA | 4.5 | 67 | DNA | 13.4 | 1343 | 241 | 0.13 | 0.010522 |  | 1.362 |  | 617 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01117042/DNA | 4.5 | 67 | DNA | 16.5 | 1885 | 338 | 0.19 | 0.0048279 |  | 1.362 |  | 866 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01119014/DNA | 4.5 | 75 | DNA | 5.5 | 738 | 118 | 0.07 | 0.0008654 |  | 1.362 |  | 339 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01119018/DNA | 4.5 | 75 | DNA | 7.1 | 875 | 140 | 0.09 | 0.0028568 |  | 1.362 |  | 402 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01119026/DNA | 4.5 | 75 | DNA | 10.2 | 1180 | 189 | 0.12 | 0.0048443 |  | 1.362 |  | 542 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01119034/DNA | 4.5 | 75 | DNA | 13.4 | 1532 | 246 | 0.15 | 0.014513 |  | 1.362 |  | 704 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01119042/DNA | 4.5 | 75 | DNA | 16.5 | 2155 | 346 | 0.22 | 0.0067993 |  | 1.362 |  | 990 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01121014/DNA | 4.5 | 82.5 | DNA | 5.5 | 829 | 120 | 0.08 | 0.0012136 |  | 1.362 |  | 381 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01121018/DNA | 4.5 | 82.5 | DNA | 7.1 | 984 | 143 | 0.1 | 0.003794 |  | 1.362 |  | 452 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01121026/DNA | 4.5 | 82.5 | DNA | 10.2 | 1328 | 193 | 0.13 | 0.006136 |  | 1.362 |  | 610 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01121034/DNA | 4.5 | 82.5 | DNA | 13.4 | 1724 | 250 | 0.17 | 0.019256 |  | 1.362 |  | 792 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01121042/DNA | 4.5 | 82.5 | DNA | 16.5 | 2425 | 352 | 0.24 | 0.0085222 |  | 1.362 |  | 1114 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01123014/DNA | 4.5 | 90.5 | DNA | 5.5 | 923 | 122 | 0.09 | 0.0016402 |  | 1.362 |  | 424 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01123018/DNA | 4.5 | 90.5 | DNA | 7.1 | 1093 | 145 | 0.11 | 0.0049066 |  | 1.362 |  | 502 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01123026/DNA | 4.5 | 90.5 | DNA | 10.2 | 1476 | 196 | 0.15 | 0.0086548 |  | 1.362 |  | 678 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01123034/DNA | 4.5 | 90.5 | DNA | 13.4 | 1918 | 254 | 0.19 | 0.024783 |  | 1.362 |  | 881 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01123042/DNA | 4.5 | 90.5 | DNA | 16.5 | 2695 | 357 | 0.27 | 0.011248 |  | 1.362 |  | 1238 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01125014/DNA | 4.5 | 98.5 | DNA | 5.5 | 1014 | 124 | 0.1 | 0.0021524 |  | 1.362 |  | 466 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01125018/DNA | 4.5 | 98.5 | DNA | 7.1 | 1202 | 147 | 0.12 | 0.0062074 |  | 1.362 |  | 552 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01125026/DNA | 4.5 | 98.5 | DNA | 10.2 | 1624 | 198 | 0.16 | 0.010501 |  | 1.362 |  | 746 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01125034/DNA | 4.5 | 98.5 | DNA | 13.4 | 2107 | 257 | 0.21 | 0.031126 |  | 1.362 |  | 968 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01125042/DNA | 4.5 | 98.5 | DNA | 16.5 | 2965 | 361 | 0.3 | 0.014443 |  | 1.362 |  | 1362 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01127014/DNA | 4.5 | 106.5 | DNA | 5.5 | 1106 | 125 | 0.11 | 0.0027571 |  | 1.362 |  | 508 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01127018/DNA | 4.5 | 106.5 | DNA | 7.1 | 1313 | 148 | 0.13 | 0.0077091 |  | 1.362 |  | 603 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01127026/DNA | 4.5 | 106.5 | DNA | 10.2 | 1772 | 200 | 0.18 | 0.013963 |  | 1.362 |  | 814 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01127034/DNA | 4.5 | 106.5 | DNA | 13.4 | 2301 | 260 | 0.23 | 0.038313 |  | 1.362 |  | 1057 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01127042/DNA | 4.5 | 106.5 | DNA | 16.5 | 3232 | 365 | 0.32 | 0.017141 |  | 1.362 |  | 1485 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01129014/DNA | 4.5 | 114 | DNA | 5.5 | 1199 | 126 | 0.12 | 0.0034613 |  | 1.362 |  | 551 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01129018/DNA | 4.5 | 114 | DNA | 7.1 | 1421 | 149 | 0.14 | 0.009424 |  | 1.362 |  | 653 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01129026/DNA | 4.5 | 114 | DNA | 10.2 | 1920 | 202 | 0.19 | 0.016447 |  | 1.362 |  | 882 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01129034/DNA | 4.5 | 114 | DNA | 13.4 | 2492 | 262 | 0.25 | 0.046372 |  | 1.362 |  | 1145 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01129042/DNA | 4.5 | 114 | DNA | 16.5 | 3502 | 368 | 0.35 | 0.021229 |  | 1.362 |  | 1609 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01131014/DNA | 4.5 | 122 | DNA | 5.5 | 1293 | 127 | 0.13 | 0.0042719 |  | 1.362 |  | 594 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01131018/DNA | 4.5 | 122 | DNA | 7.1 | 1530 | 150 | 0.15 | 0.011364 |  | 1.362 |  | 703 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01131026/DNA | 4.5 | 122 | DNA | 10.2 | 2066 | 203 | 0.21 | 0.02098 |  | 1.362 |  | 949 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01131034/DNA | 4.5 | 122 | DNA | 13.4 | 2684 | 264 | 0.27 | 0.05533 |  | 1.362 |  | 1233 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01131042/DNA | 4.5 | 122 | DNA | 16.5 | 3770 | 371 | 0.38 | 0.025861 |  | 1.362 |  | 1732 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01133014/DNA | 4.5 | 130 | DNA | 5.5 | 1382 | 128 | 0.14 | 0.0051957 |  | 1.362 |  | 635 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01133018/DNA | 4.5 | 130 | DNA | 7.1 | 1641 | 152 | 0.16 | 0.013542 |  | 1.362 |  | 754 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01133026/DNA | 4.5 | 130 | DNA | 10.2 | 2214 | 204 | 0.22 | 0.024181 |  | 1.362 |  | 1017 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01133034/DNA | 4.5 | 130 | DNA | 13.4 | 2875 | 266 | 0.29 | 0.065213 |  | 1.362 |  | 1321 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01133042/DNA | 4.5 | 130 | DNA | 16.5 | 4042 | 373 | 0.4 | 0.029696 |  | 1.362 |  | 1857 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01135014/DNA | 4.5 | 138 | DNA | 5.5 | 1476 | 129 | 0.15 | 0.0062396 |  | 1.362 |  | 678 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01135018/DNA | 4.5 | 138 | DNA | 7.1 | 1748 | 152 | 0.17 | 0.015969 |  | 1.362 |  | 803 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01135026/DNA | 4.5 | 138 | DNA | 10.2 | 2362 | 206 | 0.24 | 0.029906 |  | 1.362 |  | 1085 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01135034/DNA | 4.5 | 138 | DNA | 13.4 | 3065 | 267 | 0.31 | 0.076044 |  | 1.362 |  | 1408 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01135042/DNA | 4.5 | 138 | DNA | 16.5 | 4312 | 376 | 0.43 | 0.035351 |  | 1.362 |  | 1981 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01137014/DNA | 4.5 | 145.5 | DNA | 5.5 | 1569 | 129 | 0.16 | 0.0074102 |  | 1.362 |  | 721 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01137018/DNA | 4.5 | 145.5 | DNA | 7.1 | 1861 | 153 | 0.19 | 0.020584 |  | 1.362 |  | 855 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01137026/DNA | 4.5 | 145.5 | DNA | 10.2 | 2508 | 207 | 0.25 | 0.033903 |  | 1.362 |  | 1152 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01137034/DNA | 4.5 | 145.5 | DNA | 13.4 | 3261 | 269 | 0.33 | 0.087847 |  | 1.362 |  | 1498 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01137042/DNA | 4.5 | 145.5 | DNA | 16.5 | 4580 | 377 | 0.46 | 0.041621 |  | 1.362 |  | 2104 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01139014/DNA | 4.5 | 153.5 | DNA | 5.5 | 1659 | 130 | 0.17 | 0.0087143 |  | 1.362 |  | 762 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01139018/DNA | 4.5 | 153.5 | DNA | 7.1 | 1968 | 154 | 0.2 | 0.023729 |  | 1.362 |  | 904 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01139026/DNA | 4.5 | 153.5 | DNA | 10.2 | 2656 | 208 | 0.27 | 0.040937 |  | 1.362 |  | 1220 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01139034/DNA | 4.5 | 153.5 | DNA | 13.4 | 3450 | 270 | 0.35 | 0.10064 |  | 1.362 |  | 1585 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01139042/DNA | 4.5 | 153.5 | DNA | 16.5 | 4850 | 379 | 0.49 | 0.048529 |  | 1.362 |  | 2228 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01141014/DNA | 4.5 | 161.5 | DNA | 5.5 | 1752 | 130 | 0.18 | 0.010158 |  | 1.362 |  | 805 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01141018/DNA | 4.5 | 161.5 | DNA | 7.1 | 2077 | 154 | 0.21 | 0.027165 |  | 1.362 |  | 954 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01141026/DNA | 4.5 | 161.5 | DNA | 10.2 | 2804 | 208 | 0.28 | 0.045806 |  | 1.362 |  | 1288 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01141034/DNA | 4.5 | 161.5 | DNA | 13.4 | 3642 | 271 | 0.36 | 0.10975 |  | 1.362 |  | 1673 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01141042/DNA | 4.5 | 161.5 | DNA | 16.5 | 5117 | 380 | 0.51 | 0.05416 |  | 1.362 |  | 2351 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01143014/DNA | 4.5 | 169.5 | DNA | 5.5 | 1846 | 131 | 0.18 | 0.010598 |  | 1.362 |  | 848 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01143018/DNA | 4.5 | 169.5 | DNA | 7.1 | 2188 | 155 | 0.22 | 0.030904 |  | 1.362 |  | 1005 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01143026/DNA | 4.5 | 169.5 | DNA | 10.2 | 2952 | 209 | 0.3 | 0.054266 |  | 1.362 |  | 1356 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01143034/DNA | 4.5 | 169.5 | DNA | 13.4 | 3835 | 272 | 0.38 | 0.12426 |  | 1.362 |  | 1762 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01143042/DNA | 4.5 | 169.5 | DNA | 16.5 | 5387 | 382 | 0.54 | 0.062256 |  | 1.362 |  | 2475 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01145014/DNA | 4.5 | 177 | DNA | 5.5 | 1935 | 131 | 0.19 | 0.012236 |  | 1.362 |  | 889 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01145018/DNA | 4.5 | 177 | DNA | 7.1 | 2294 | 155 | 0.23 | 0.034956 |  | 1.362 |  | 1054 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01145026/DNA | 4.5 | 177 | DNA | 10.2 | 3100 | 210 | 0.31 | 0.06008 |  | 1.362 |  | 1424 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01145034/DNA | 4.5 | 177 | DNA | 13.4 | 4025 | 273 | 0.4 | 0.13983 |  | 1.362 |  | 1849 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01145042/DNA | 4.5 | 177 | DNA | 16.5 | 5659 | 383 | 0.57 | 0.071057 |  | 1.362 |  | 2600 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01147014/DNA | 4.5 | 185 | DNA | 5.5 | 2029 | 132 | 0.2 | 0.01403 |  | 1.362 |  | 932 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01147018/DNA | 4.5 | 185 | DNA | 7.1 | 2407 | 156 | 0.24 | 0.039332 |  | 1.362 |  | 1106 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01147026/DNA | 4.5 | 185 | DNA | 10.2 | 3245 | 210 | 0.32 | 0.066273 |  | 1.362 |  | 1491 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01147034/DNA | 4.5 | 185 | DNA | 13.4 | 4218 | 274 | 0.42 | 0.15648 |  | 1.362 |  | 1938 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01147042/DNA | 4.5 | 185 | DNA | 16.5 | 5927 | 384 | 0.59 | 0.078175 |  | 1.362 |  | 2723 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01149014/DNA | 4.5 | 193 | DNA | 5.5 | 2122 | 132 | 0.21 | 0.015985 |  | 1.362 |  | 975 | [19 empty] | 0.00060626 | 1.8895 | 1 | 0.00030758
Build-In Floor | Mini Canal | MICL.01149018/DNA | 4.5 | 193 | DNA | 7.1 | 2514 | 156 | 0.25 | 0.044044 |  | 1.362 |  | 1155 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01149026/DNA | 4.5 | 193 | DNA | 10.2 | 3396 | 211 | 0.34 | 0.076909 |  | 1.362 |  | 1560 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01149034/DNA | 4.5 | 193 | DNA | 13.4 | 4408 | 274 | 0.44 | 0.17421 |  | 1.362 |  | 2025 | [19 empty] | 0.013163 | 1.4287 | 1 | 0.00092092
Build-In Floor | Mini Canal | MICL.01149042/DNA | 4.5 | 193 | DNA | 16.5 | 6197 | 385 | 0.62 | 0.088278 |  | 1.362 |  | 2847 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01407014/DNA | 5.5 | 27.5 | DNA | 5.5 | 209 | 91 | 0.02 | 7.1997e-05 |  | 1.362 |  | 96 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01407026/DNA | 5.5 | 27.5 | DNA | 10.2 | 364 | 158 | 0.04 | 0.00015352 |  | 1.362 |  | 167 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01407034/DNA | 5.5 | 27.5 | DNA | 13.4 | 496 | 216 | 0.05 | 0.00023499 |  | 1.362 |  | 228 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01407042/DNA | 5.5 | 27.5 | DNA | 16.5 | 668 | 291 | 0.07 | 0.00044718 |  | 1.362 |  | 307 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01408014/DNA | 5.5 | 31.5 | DNA | 5.5 | 261 | 99 | 0.03 | 0.00017329 |  | 1.362 |  | 120 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01408026/DNA | 5.5 | 31.5 | DNA | 10.2 | 455 | 173 | 0.05 | 0.00025256 |  | 1.362 |  | 209 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01408034/DNA | 5.5 | 31.5 | DNA | 13.4 | 620 | 236 | 0.06 | 0.00034883 |  | 1.362 |  | 285 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01408042/DNA | 5.5 | 31.5 | DNA | 16.5 | 836 | 319 | 0.08 | 0.00047493 |  | 1.362 |  | 384 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01409014/DNA | 5.5 | 35.5 | DNA | 5.5 | 316 | 107 | 0.03 | 0.00019229 |  | 1.362 |  | 145 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01409026/DNA | 5.5 | 35.5 | DNA | 10.2 | 544 | 184 | 0.05 | 0.00027012 |  | 1.362 |  | 250 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01409034/DNA | 5.5 | 35.5 | DNA | 13.4 | 744 | 252 | 0.07 | 0.00048696 |  | 1.362 |  | 342 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01409042/DNA | 5.5 | 35.5 | DNA | 16.5 | 1003 | 340 | 0.1 | 0.00075371 |  | 1.362 |  | 461 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01410014/DNA | 5.5 | 39.5 | DNA | 5.5 | 368 | 112 | 0.04 | 0.00036064 |  | 1.362 |  | 169 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01410026/DNA | 5.5 | 39.5 | DNA | 10.2 | 636 | 194 | 0.06 | 0.00040524 |  | 1.362 |  | 292 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01410034/DNA | 5.5 | 39.5 | DNA | 13.4 | 869 | 265 | 0.09 | 0.00081806 |  | 1.362 |  | 399 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01410042/DNA | 5.5 | 39.5 | DNA | 16.5 | 1171 | 357 | 0.12 | 0.0011016 |  | 1.362 |  | 538 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01411014/DNA | 5.5 | 43.5 | DNA | 5.5 | 418 | 116 | 0.04 | 0.00039244 |  | 1.362 |  | 192 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01411026/DNA | 5.5 | 43.5 | DNA | 10.2 | 729 | 202 | 0.07 | 0.00057312 |  | 1.362 |  | 335 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01411034/DNA | 5.5 | 43.5 | DNA | 13.4 | 993 | 275 | 0.1 | 0.001033 |  | 1.362 |  | 456 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01411042/DNA | 5.5 | 43.5 | DNA | 16.5 | 1337 | 370 | 0.13 | 0.0013164 |  | 1.362 |  | 614 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01412014/DNA | 5.5 | 47 | DNA | 5.5 | 470 | 119 | 0.05 | 0.00064111 |  | 1.362 |  | 216 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01412026/DNA | 5.5 | 47 | DNA | 10.2 | 818 | 208 | 0.08 | 0.000776 |  | 1.362 |  | 376 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01412034/DNA | 5.5 | 47 | DNA | 13.4 | 1117 | 284 | 0.11 | 0.0012769 |  | 1.362 |  | 513 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01412042/DNA | 5.5 | 47 | DNA | 16.5 | 1506 | 383 | 0.15 | 0.0017763 |  | 1.362 |  | 692 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01413014/DNA | 5.5 | 51 | DNA | 5.5 | 525 | 123 | 0.05 | 0.00068852 |  | 1.362 |  | 241 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01413026/DNA | 5.5 | 51 | DNA | 10.2 | 910 | 213 | 0.09 | 0.001016 |  | 1.362 |  | 418 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01413034/DNA | 5.5 | 51 | DNA | 13.4 | 1239 | 290 | 0.12 | 0.0015509 |  | 1.362 |  | 569 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01413042/DNA | 5.5 | 51 | DNA | 16.5 | 1672 | 392 | 0.17 | 0.0023114 |  | 1.362 |  | 768 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01415014/DNA | 5.5 | 59 | DNA | 5.5 | 629 | 128 | 0.06 | 0.0010958 |  | 1.362 |  | 289 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01415026/DNA | 5.5 | 59 | DNA | 10.2 | 1091 | 222 | 0.11 | 0.0016159 |  | 1.362 |  | 501 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01415034/DNA | 5.5 | 59 | DNA | 13.4 | 1489 | 303 | 0.15 | 0.0025026 |  | 1.362 |  | 684 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01415042/DNA | 5.5 | 59 | DNA | 16.5 | 2007 | 408 | 0.2 | 0.0032892 |  | 1.362 |  | 922 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01417014/DNA | 5.5 | 67 | DNA | 5.5 | 734 | 132 | 0.07 | 0.0016288 |  | 1.362 |  | 337 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01417026/DNA | 5.5 | 67 | DNA | 10.2 | 1273 | 228 | 0.13 | 0.0023887 |  | 1.362 |  | 585 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01417034/DNA | 5.5 | 67 | DNA | 13.4 | 1735 | 311 | 0.17 | 0.0033299 |  | 1.362 |  | 797 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01417042/DNA | 5.5 | 67 | DNA | 16.5 | 2340 | 420 | 0.23 | 0.0044638 |  | 1.362 |  | 1075 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01419014/DNA | 5.5 | 75 | DNA | 5.5 | 838 | 134 | 0.08 | 0.0023018 |  | 1.362 |  | 385 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01419026/DNA | 5.5 | 75 | DNA | 10.2 | 1454 | 233 | 0.15 | 0.0033498 |  | 1.362 |  | 668 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01419034/DNA | 5.5 | 75 | DNA | 13.4 | 1985 | 318 | 0.2 | 0.0047394 |  | 1.362 |  | 912 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01419042/DNA | 5.5 | 75 | DNA | 16.5 | 2675 | 429 | 0.27 | 0.006285 |  | 1.362 |  | 1229 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01421014/DNA | 5.5 | 82.5 | DNA | 5.5 | 943 | 137 | 0.09 | 0.0031283 |  | 1.362 |  | 433 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01421026/DNA | 5.5 | 82.5 | DNA | 10.2 | 1637 | 238 | 0.16 | 0.0040378 |  | 1.362 |  | 752 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01421034/DNA | 5.5 | 82.5 | DNA | 13.4 | 2231 | 324 | 0.22 | 0.0059148 |  | 1.362 |  | 1025 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01421042/DNA | 5.5 | 82.5 | DNA | 16.5 | 3008 | 437 | 0.3 | 0.0079398 |  | 1.362 |  | 1382 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01423014/DNA | 5.5 | 90.5 | DNA | 5.5 | 1047 | 139 | 0.1 | 0.0041219 |  | 1.362 |  | 481 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01423026/DNA | 5.5 | 90.5 | DNA | 10.2 | 1818 | 241 | 0.18 | 0.0053389 |  | 1.362 |  | 835 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01423034/DNA | 5.5 | 90.5 | DNA | 13.4 | 2481 | 329 | 0.25 | 0.00783 |  | 1.362 |  | 1140 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01423042/DNA | 5.5 | 90.5 | DNA | 16.5 | 3343 | 443 | 0.33 | 0.009819 |  | 1.362 |  | 1536 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01425014/DNA | 5.5 | 98.5 | DNA | 5.5 | 1154 | 141 | 0.12 | 0.0062074 |  | 1.362 |  | 530 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01425026/DNA | 5.5 | 98.5 | DNA | 10.2 | 2000 | 244 | 0.2 | 0.0068668 |  | 1.362 |  | 919 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01425034/DNA | 5.5 | 98.5 | DNA | 13.4 | 2727 | 332 | 0.27 | 0.0093893 |  | 1.362 |  | 1253 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01425042/DNA | 5.5 | 98.5 | DNA | 16.5 | 3679 | 449 | 0.37 | 0.012573 |  | 1.362 |  | 1690 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01427014/DNA | 5.5 | 106.5 | DNA | 5.5 | 1256 | 142 | 0.13 | 0.0077091 |  | 1.362 |  | 577 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01427026/DNA | 5.5 | 106.5 | DNA | 10.2 | 2183 | 246 | 0.22 | 0.0086352 |  | 1.362 |  | 1003 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01427034/DNA | 5.5 | 106.5 | DNA | 13.4 | 2976 | 336 | 0.3 | 0.011855 |  | 1.362 |  | 1367 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01427042/DNA | 5.5 | 106.5 | DNA | 16.5 | 4012 | 453 | 0.4 | 0.01499 |  | 1.362 |  | 1843 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01429014/DNA | 5.5 | 114 | DNA | 5.5 | 1363 | 143 | 0.14 | 0.009424 |  | 1.362 |  | 626 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01429026/DNA | 5.5 | 114 | DNA | 10.2 | 2362 | 248 | 0.24 | 0.010657 |  | 1.362 |  | 1085 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01429034/DNA | 5.5 | 114 | DNA | 13.4 | 3224 | 339 | 0.32 | 0.013832 |  | 1.362 |  | 1481 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01429042/DNA | 5.5 | 114 | DNA | 16.5 | 4345 | 457 | 0.43 | 0.017658 |  | 1.362 |  | 1996 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01431014/DNA | 5.5 | 122 | DNA | 5.5 | 1465 | 144 | 0.15 | 0.011364 |  | 1.362 |  | 673 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01431026/DNA | 5.5 | 122 | DNA | 10.2 | 2547 | 250 | 0.25 | 0.012054 |  | 1.362 |  | 1170 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01431034/DNA | 5.5 | 122 | DNA | 13.4 | 3472 | 341 | 0.35 | 0.01689 |  | 1.362 |  | 1595 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01431042/DNA | 5.5 | 122 | DNA | 16.5 | 4680 | 460 | 0.47 | 0.021442 |  | 1.362 |  | 2150 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01433014/DNA | 5.5 | 130 | DNA | 5.5 | 1572 | 145 | 0.16 | 0.013542 |  | 1.362 |  | 722 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01433026/DNA | 5.5 | 130 | DNA | 10.2 | 2727 | 252 | 0.27 | 0.014521 |  | 1.362 |  | 1253 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01433034/DNA | 5.5 | 130 | DNA | 13.4 | 3720 | 344 | 0.37 | 0.019317 |  | 1.362 |  | 1709 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01433042/DNA | 5.5 | 130 | DNA | 16.5 | 5015 | 463 | 0.5 | 0.0247 |  | 1.362 |  | 2304 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01435014/DNA | 5.5 | 138 | DNA | 5.5 | 1676 | 146 | 0.17 | 0.015969 |  | 1.362 |  | 770 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01435026/DNA | 5.5 | 138 | DNA | 10.2 | 2908 | 253 | 0.29 | 0.017277 |  | 1.362 |  | 1336 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01435034/DNA | 5.5 | 138 | DNA | 13.4 | 3970 | 346 | 0.4 | 0.023009 |  | 1.362 |  | 1824 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01435042/DNA | 5.5 | 138 | DNA | 16.5 | 5348 | 466 | 0.53 | 0.028232 |  | 1.362 |  | 2457 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01437014/DNA | 5.5 | 145.5 | DNA | 5.5 | 1781 | 147 | 0.18 | 0.018657 |  | 1.362 |  | 818 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01437026/DNA | 5.5 | 145.5 | DNA | 10.2 | 3091 | 255 | 0.31 | 0.020332 |  | 1.362 |  | 1420 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01437034/DNA | 5.5 | 145.5 | DNA | 13.4 | 4216 | 347 | 0.42 | 0.025916 |  | 1.362 |  | 1937 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01437042/DNA | 5.5 | 145.5 | DNA | 16.5 | 5683 | 468 | 0.57 | 0.033137 |  | 1.362 |  | 2611 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01439014/DNA | 5.5 | 153.5 | DNA | 5.5 | 1885 | 147 | 0.19 | 0.021618 |  | 1.362 |  | 866 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01439026/DNA | 5.5 | 153.5 | DNA | 10.2 | 3274 | 256 | 0.33 | 0.023699 |  | 1.362 |  | 1504 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01439034/DNA | 5.5 | 153.5 | DNA | 13.4 | 4467 | 349 | 0.45 | 0.030281 |  | 1.362 |  | 2052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01439042/DNA | 5.5 | 153.5 | DNA | 16.5 | 6016 | 470 | 0.6 | 0.037311 |  | 1.362 |  | 2764 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01441014/DNA | 5.5 | 161.5 | DNA | 5.5 | 1990 | 148 | 0.2 | 0.024862 |  | 1.362 |  | 914 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01441026/DNA | 5.5 | 161.5 | DNA | 10.2 | 3454 | 257 | 0.35 | 0.027391 |  | 1.362 |  | 1587 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01441034/DNA | 5.5 | 161.5 | DNA | 13.4 | 4713 | 350 | 0.47 | 0.033699 |  | 1.362 |  | 2165 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01441042/DNA | 5.5 | 161.5 | DNA | 16.5 | 6352 | 472 | 0.64 | 0.043042 |  | 1.362 |  | 2918 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01443014/DNA | 5.5 | 169.5 | DNA | 5.5 | 2094 | 148 | 0.21 | 0.028402 |  | 1.362 |  | 962 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01443026/DNA | 5.5 | 169.5 | DNA | 10.2 | 3635 | 258 | 0.36 | 0.029901 |  | 1.362 |  | 1670 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01443034/DNA | 5.5 | 169.5 | DNA | 13.4 | 4961 | 352 | 0.5 | 0.038774 |  | 1.362 |  | 2279 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01443042/DNA | 5.5 | 169.5 | DNA | 16.5 | 6687 | 474 | 0.67 | 0.047891 |  | 1.362 |  | 3072 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01445014/DNA | 5.5 | 177 | DNA | 5.5 | 2201 | 149 | 0.22 | 0.032248 |  | 1.362 |  | 1011 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01445026/DNA | 5.5 | 177 | DNA | 10.2 | 3818 | 259 | 0.38 | 0.034153 |  | 1.362 |  | 1754 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01445034/DNA | 5.5 | 177 | DNA | 13.4 | 5209 | 353 | 0.52 | 0.042731 |  | 1.362 |  | 2393 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01445042/DNA | 5.5 | 177 | DNA | 16.5 | 7020 | 475 | 0.7 | 0.05305 |  | 1.362 |  | 3225 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01447014/DNA | 5.5 | 185 | DNA | 5.5 | 2303 | 149 | 0.23 | 0.036411 |  | 1.362 |  | 1058 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01447026/DNA | 5.5 | 185 | DNA | 10.2 | 4001 | 259 | 0.4 | 0.038759 |  | 1.362 |  | 1838 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01447034/DNA | 5.5 | 185 | DNA | 13.4 | 5455 | 354 | 0.55 | 0.048554 |  | 1.362 |  | 2506 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01447042/DNA | 5.5 | 185 | DNA | 16.5 | 7355 | 477 | 0.74 | 0.060044 |  | 1.362 |  | 3379 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01449014/DNA | 5.5 | 193 | DNA | 5.5 | 2410 | 150 | 0.24 | 0.040903 |  | 1.362 |  | 1107 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Build-In Floor | Mini Canal | MICL.01449026/DNA | 5.5 | 193 | DNA | 10.2 | 4181 | 260 | 0.42 | 0.043732 |  | 1.362 |  | 1921 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01449034/DNA | 5.5 | 193 | DNA | 13.4 | 5705 | 355 | 0.57 | 0.053078 |  | 1.362 |  | 2621 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01449042/DNA | 5.5 | 193 | DNA | 16.5 | 7690 | 478 | 0.77 | 0.065925 |  | 1.362 |  | 3533 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01907026/DNA | 7.5 | 27.5 | DNA | 10.2 | 414 | 180 | 0.04 | 0.00015352 |  | 1.362 |  | 190 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01907034/DNA | 7.5 | 27.5 | DNA | 13.4 | 559 | 243 | 0.06 | 0.00033294 |  | 1.362 |  | 257 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01907042/DNA | 7.5 | 27.5 | DNA | 16.5 | 766 | 334 | 0.08 | 0.00057754 |  | 1.362 |  | 352 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01908026/DNA | 7.5 | 31.5 | DNA | 10.2 | 518 | 197 | 0.05 | 0.00025256 |  | 1.362 |  | 238 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01908034/DNA | 7.5 | 31.5 | DNA | 13.4 | 701 | 267 | 0.07 | 0.00047091 |  | 1.362 |  | 322 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01908042/DNA | 7.5 | 31.5 | DNA | 16.5 | 960 | 366 | 0.1 | 0.00073565 |  | 1.362 |  | 441 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01909026/DNA | 7.5 | 35.5 | DNA | 10.2 | 618 | 209 | 0.06 | 0.00038114 |  | 1.362 |  | 284 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01909034/DNA | 7.5 | 35.5 | DNA | 13.4 | 838 | 284 | 0.08 | 0.00063105 |  | 1.362 |  | 385 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01909042/DNA | 7.5 | 35.5 | DNA | 16.5 | 1154 | 391 | 0.12 | 0.0010769 |  | 1.362 |  | 530 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01910026/DNA | 7.5 | 39.5 | DNA | 10.2 | 723 | 220 | 0.07 | 0.00054163 |  | 1.362 |  | 332 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01910034/DNA | 7.5 | 39.5 | DNA | 13.4 | 977 | 298 | 0.1 | 0.0010033 |  | 1.362 |  | 449 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01910042/DNA | 7.5 | 39.5 | DNA | 16.5 | 1343 | 409 | 0.13 | 0.0012881 |  | 1.362 |  | 617 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01911026/DNA | 7.5 | 43.5 | DNA | 10.2 | 827 | 229 | 0.08 | 0.00073631 |  | 1.362 |  | 380 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01911034/DNA | 7.5 | 43.5 | DNA | 13.4 | 1119 | 310 | 0.11 | 0.001242 |  | 1.362 |  | 514 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01911042/DNA | 7.5 | 43.5 | DNA | 16.5 | 1537 | 426 | 0.15 | 0.00174 |  | 1.362 |  | 706 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01912026/DNA | 7.5 | 47 | DNA | 10.2 | 929 | 236 | 0.09 | 0.00096734 |  | 1.362 |  | 427 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01912034/DNA | 7.5 | 47 | DNA | 13.4 | 1258 | 320 | 0.13 | 0.0017624 |  | 1.362 |  | 578 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01912042/DNA | 7.5 | 47 | DNA | 16.5 | 1726 | 438 | 0.17 | 0.0022664 |  | 1.362 |  | 793 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01913026/DNA | 7.5 | 51 | DNA | 10.2 | 1032 | 242 | 0.1 | 0.0012369 |  | 1.362 |  | 474 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01913034/DNA | 7.5 | 51 | DNA | 13.4 | 1397 | 328 | 0.14 | 0.0020866 |  | 1.362 |  | 642 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01913042/DNA | 7.5 | 51 | DNA | 16.5 | 1920 | 450 | 0.19 | 0.0028691 |  | 1.362 |  | 882 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01915026/DNA | 7.5 | 59 | DNA | 10.2 | 1239 | 252 | 0.12 | 0.0018995 |  | 1.362 |  | 569 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01915034/DNA | 7.5 | 59 | DNA | 13.4 | 1678 | 341 | 0.17 | 0.0031817 |  | 1.362 |  | 771 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01915042/DNA | 7.5 | 59 | DNA | 16.5 | 2303 | 468 | 0.23 | 0.0043123 |  | 1.362 |  | 1058 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01917026/DNA | 7.5 | 67 | DNA | 10.2 | 1445 | 259 | 0.14 | 0.00274 |  | 1.362 |  | 664 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01917034/DNA | 7.5 | 67 | DNA | 13.4 | 1957 | 351 | 0.2 | 0.0045433 |  | 1.362 |  | 899 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01917042/DNA | 7.5 | 67 | DNA | 16.5 | 2688 | 482 | 0.27 | 0.0060852 |  | 1.362 |  | 1235 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01919026/DNA | 7.5 | 75 | DNA | 10.2 | 1652 | 265 | 0.17 | 0.0042206 |  | 1.362 |  | 759 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01919034/DNA | 7.5 | 75 | DNA | 13.4 | 2235 | 359 | 0.22 | 0.0056837 |  | 1.362 |  | 1027 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01919042/DNA | 7.5 | 75 | DNA | 16.5 | 3071 | 493 | 0.31 | 0.0082029 |  | 1.362 |  | 1411 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01921026/DNA | 7.5 | 82.5 | DNA | 10.2 | 1861 | 270 | 0.19 | 0.0055397 |  | 1.362 |  | 855 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01921034/DNA | 7.5 | 82.5 | DNA | 13.4 | 2516 | 365 | 0.25 | 0.0075419 |  | 1.362 |  | 1156 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01921042/DNA | 7.5 | 82.5 | DNA | 16.5 | 3457 | 502 | 0.35 | 0.01068 |  | 1.362 |  | 1588 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01923026/DNA | 7.5 | 90.5 | DNA | 10.2 | 2066 | 274 | 0.21 | 0.007085 |  | 1.362 |  | 949 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01923034/DNA | 7.5 | 90.5 | DNA | 13.4 | 2795 | 370 | 0.28 | 0.0097075 |  | 1.362 |  | 1284 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01923042/DNA | 7.5 | 90.5 | DNA | 16.5 | 3840 | 509 | 0.38 | 0.012872 |  | 1.362 |  | 1764 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01925026/DNA | 7.5 | 98.5 | DNA | 10.2 | 2272 | 277 | 0.23 | 0.00887 |  | 1.362 |  | 1044 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01925034/DNA | 7.5 | 98.5 | DNA | 13.4 | 3076 | 375 | 0.31 | 0.012194 |  | 1.362 |  | 1413 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01925042/DNA | 7.5 | 98.5 | DNA | 16.5 | 4225 | 515 | 0.42 | 0.016028 |  | 1.362 |  | 1941 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01927026/DNA | 7.5 | 106.5 | DNA | 10.2 | 2479 | 280 | 0.25 | 0.010908 |  | 1.362 |  | 1139 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01927034/DNA | 7.5 | 106.5 | DNA | 13.4 | 3356 | 379 | 0.34 | 0.015016 |  | 1.362 |  | 1542 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01927042/DNA | 7.5 | 106.5 | DNA | 16.5 | 4608 | 520 | 0.46 | 0.019582 |  | 1.362 |  | 2117 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01929026/DNA | 7.5 | 114 | DNA | 10.2 | 2684 | 282 | 0.27 | 0.013212 |  | 1.362 |  | 1233 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01929034/DNA | 7.5 | 114 | DNA | 13.4 | 3633 | 382 | 0.36 | 0.017269 |  | 1.362 |  | 1669 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01929042/DNA | 7.5 | 114 | DNA | 16.5 | 4993 | 525 | 0.5 | 0.023546 |  | 1.362 |  | 2294 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01931026/DNA | 7.5 | 122 | DNA | 10.2 | 2893 | 284 | 0.29 | 0.015794 |  | 1.362 |  | 1329 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01931034/DNA | 7.5 | 122 | DNA | 13.4 | 3914 | 385 | 0.39 | 0.020703 |  | 1.362 |  | 1798 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01931042/DNA | 7.5 | 122 | DNA | 16.5 | 5379 | 529 | 0.54 | 0.027934 |  | 1.362 |  | 2471 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01933026/DNA | 7.5 | 130 | DNA | 10.2 | 3097 | 286 | 0.31 | 0.018668 |  | 1.362 |  | 1423 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01933034/DNA | 7.5 | 130 | DNA | 13.4 | 4195 | 387 | 0.42 | 0.024507 |  | 1.362 |  | 1927 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01933042/DNA | 7.5 | 130 | DNA | 16.5 | 5760 | 532 | 0.58 | 0.032757 |  | 1.362 |  | 2646 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01935026/DNA | 7.5 | 138 | DNA | 10.2 | 3304 | 288 | 0.33 | 0.021845 |  | 1.362 |  | 1518 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01935034/DNA | 7.5 | 138 | DNA | 13.4 | 4473 | 390 | 0.45 | 0.028694 |  | 1.362 |  | 2055 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01935042/DNA | 7.5 | 138 | DNA | 16.5 | 6145 | 535 | 0.61 | 0.036871 |  | 1.362 |  | 2823 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01937026/DNA | 7.5 | 145.5 | DNA | 10.2 | 3511 | 289 | 0.35 | 0.025337 |  | 1.362 |  | 1613 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01937034/DNA | 7.5 | 145.5 | DNA | 13.4 | 4754 | 392 | 0.48 | 0.033275 |  | 1.362 |  | 2184 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01937042/DNA | 7.5 | 145.5 | DNA | 16.5 | 6528 | 538 | 0.65 | 0.042509 |  | 1.362 |  | 2999 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01939026/DNA | 7.5 | 153.5 | DNA | 10.2 | 3716 | 290 | 0.37 | 0.029156 |  | 1.362 |  | 1707 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01939034/DNA | 7.5 | 153.5 | DNA | 13.4 | 5033 | 393 | 0.5 | 0.036871 |  | 1.362 |  | 2312 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01939042/DNA | 7.5 | 153.5 | DNA | 16.5 | 6913 | 540 | 0.69 | 0.048616 |  | 1.362 |  | 3176 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01941026/DNA | 7.5 | 161.5 | DNA | 10.2 | 3925 | 292 | 0.39 | 0.033313 |  | 1.362 |  | 1803 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01941034/DNA | 7.5 | 161.5 | DNA | 13.4 | 5313 | 395 | 0.53 | 0.042168 |  | 1.362 |  | 2441 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01941042/DNA | 7.5 | 161.5 | DNA | 16.5 | 7296 | 542 | 0.73 | 0.055203 |  | 1.362 |  | 3352 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01943026/DNA | 7.5 | 169.5 | DNA | 10.2 | 4129 | 293 | 0.41 | 0.037821 |  | 1.362 |  | 1897 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01943034/DNA | 7.5 | 169.5 | DNA | 13.4 | 5594 | 397 | 0.56 | 0.047893 |  | 1.362 |  | 2570 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01943042/DNA | 7.5 | 169.5 | DNA | 16.5 | 7682 | 545 | 0.77 | 0.062283 |  | 1.362 |  | 3529 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01945026/DNA | 7.5 | 177 | DNA | 10.2 | 4336 | 294 | 0.43 | 0.04269 |  | 1.362 |  | 1992 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01945034/DNA | 7.5 | 177 | DNA | 13.4 | 5873 | 398 | 0.59 | 0.054055 |  | 1.362 |  | 2698 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01945042/DNA | 7.5 | 177 | DNA | 16.5 | 8065 | 546 | 0.81 | 0.069866 |  | 1.362 |  | 3705 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01947026/DNA | 7.5 | 185 | DNA | 10.2 | 4543 | 295 | 0.45 | 0.047931 |  | 1.362 |  | 2087 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01947034/DNA | 7.5 | 185 | DNA | 13.4 | 6154 | 399 | 0.62 | 0.060666 |  | 1.362 |  | 2827 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01947042/DNA | 7.5 | 185 | DNA | 16.5 | 8448 | 548 | 0.84 | 0.076242 |  | 1.362 |  | 3881 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Build-In Floor | Mini Canal | MICL.01949026/DNA | 7.5 | 193 | DNA | 10.2 | 4750 | 295 | 0.48 | 0.055627 |  | 1.362 |  | 2182 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Build-In Floor | Mini Canal | MICL.01949034/DNA | 7.5 | 193 | DNA | 13.4 | 6432 | 400 | 0.64 | 0.065814 |  | 1.362 |  | 2955 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Build-In Floor | Mini Canal | MICL.01949042/DNA | 7.5 | 193 | DNA | 16.5 | 8833 | 549 | 0.88 | 0.08476 |  | 1.362 |  | 4058 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.00806009/FS | 3 | 23.5 | 09 | 5.1 | 545 | 277 | 0.05 | 0.00016938 |  | 1.418 |  | 255 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00806014/FS | 3 | 23.5 | 14 | 7.1 | 889 | 452 | 0.09 | 0.00059966 |  | 1.418 |  | 416 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00806019/FS | 3 | 23.5 | 19 | 9.1 | 1222 | 621 | 0.12 | 0.00081905 |  | 1.418 |  | 572 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00807009/FS | 3 | 27.5 | 09 | 5.1 | 637 | 277 | 0.06 | 0.00025049 |  | 1.418 |  | 298 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00807014/FS | 3 | 27.5 | 14 | 7.1 | 1039 | 452 | 0.1 | 0.00075176 |  | 1.418 |  | 486 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00807019/FS | 3 | 27.5 | 19 | 9.1 | 1425 | 620 | 0.14 | 0.0011268 |  | 1.418 |  | 667 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00808009/FS | 3 | 31.5 | 09 | 5.1 | 727 | 277 | 0.07 | 0.00034965 |  | 1.418 |  | 340 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00808014/FS | 3 | 31.5 | 14 | 7.1 | 1186 | 452 | 0.12 | 0.001096 |  | 1.418 |  | 555 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00808019/FS | 3 | 31.5 | 19 | 9.1 | 1628 | 620 | 0.16 | 0.0014868 |  | 1.418 |  | 762 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00809009/FS | 3 | 35.5 | 09 | 5.1 | 818 | 277 | 0.08 | 0.00046778 |  | 1.418 |  | 383 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00809014/FS | 3 | 35.5 | 14 | 7.1 | 1336 | 452 | 0.13 | 0.0013042 |  | 1.418 |  | 625 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00809019/FS | 3 | 35.5 | 19 | 9.1 | 1833 | 621 | 0.18 | 0.0019 |  | 1.418 |  | 858 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00810009/FS | 3 | 39.5 | 09 | 5.1 | 908 | 277 | 0.09 | 0.00060579 |  | 1.418 |  | 425 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00810014/FS | 3 | 39.5 | 14 | 7.1 | 1483 | 452 | 0.15 | 0.0017558 |  | 1.418 |  | 694 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00810019/FS | 3 | 39.5 | 19 | 9.1 | 2036 | 621 | 0.2 | 0.0023674 |  | 1.418 |  | 953 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00811009/FS | 3 | 43.5 | 09 | 5.1 | 1000 | 277 | 0.1 | 0.00076457 |  | 1.418 |  | 468 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00811014/FS | 3 | 43.5 | 14 | 7.1 | 1630 | 452 | 0.16 | 0.0020233 |  | 1.418 |  | 763 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00811019/FS | 3 | 43.5 | 19 | 9.1 | 2239 | 620 | 0.22 | 0.0028902 |  | 1.418 |  | 1048 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00812009/FS | 3 | 47 | 09 | 5.1 | 1090 | 277 | 0.11 | 0.00094498 |  | 1.418 |  | 510 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00812014/FS | 3 | 47 | 14 | 7.1 | 1780 | 452 | 0.18 | 0.0025872 |  | 1.418 |  | 833 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00812019/FS | 3 | 47 | 19 | 9.1 | 2445 | 621 | 0.24 | 0.0034693 |  | 1.418 |  | 1144 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00814009/FS | 3 | 55 | 09 | 5.1 | 1271 | 277 | 0.13 | 0.0013741 |  | 1.418 |  | 595 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00814014/FS | 3 | 55 | 14 | 7.1 | 2077 | 452 | 0.21 | 0.0035981 |  | 1.418 |  | 972 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00814019/FS | 3 | 55 | 19 | 9.1 | 2851 | 621 | 0.29 | 0.0051432 |  | 1.418 |  | 1334 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00816009/FS | 3 | 63 | 09 | 5.1 | 1453 | 277 | 0.15 | 0.0018999 |  | 1.418 |  | 680 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00816014/FS | 3 | 63 | 14 | 7.1 | 2372 | 452 | 0.24 | 0.0047958 |  | 1.418 |  | 1110 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00816019/FS | 3 | 63 | 19 | 9.1 | 3259 | 621 | 0.33 | 0.0067639 |  | 1.418 |  | 1525 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00818009/FS | 3 | 71 | 09 | 5.1 | 1635 | 277 | 0.16 | 0.0022473 |  | 1.418 |  | 765 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00818014/FS | 3 | 71 | 14 | 7.1 | 2669 | 452 | 0.27 | 0.0061874 |  | 1.418 |  | 1249 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00818019/FS | 3 | 71 | 19 | 9.1 | 3665 | 621 | 0.37 | 0.0086293 |  | 1.418 |  | 1715 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00820009/FS | 3 | 78.5 | 09 | 5.1 | 1816 | 277 | 0.18 | 0.0029415 |  | 1.418 |  | 850 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00820014/FS | 3 | 78.5 | 14 | 7.1 | 2966 | 452 | 0.3 | 0.0077799 |  | 1.418 |  | 1388 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00820019/FS | 3 | 78.5 | 19 | 9.1 | 4073 | 621 | 0.41 | 0.010746 |  | 1.418 |  | 1906 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00822009/FS | 3 | 86.5 | 09 | 5.1 | 1998 | 277 | 0.2 | 0.0037496 |  | 1.418 |  | 935 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00822014/FS | 3 | 86.5 | 14 | 7.1 | 3263 | 452 | 0.33 | 0.0095801 |  | 1.418 |  | 1527 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00822019/FS | 3 | 86.5 | 19 | 9.1 | 4481 | 621 | 0.45 | 0.013122 |  | 1.418 |  | 2097 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00824009/FS | 3 | 94.5 | 09 | 5.1 | 2180 | 277 | 0.22 | 0.0046778 |  | 1.418 |  | 1020 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00824014/FS | 3 | 94.5 | 14 | 7.1 | 3560 | 452 | 0.36 | 0.011594 |  | 1.418 |  | 1666 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00824019/FS | 3 | 94.5 | 19 | 9.1 | 4887 | 621 | 0.49 | 0.015762 |  | 1.418 |  | 2287 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00826009/FS | 3 | 102.5 | 09 | 5.1 | 2361 | 277 | 0.24 | 0.0057322 |  | 1.418 |  | 1105 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00826014/FS | 3 | 102.5 | 14 | 7.1 | 3855 | 452 | 0.39 | 0.013829 |  | 1.418 |  | 1804 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00826019/FS | 3 | 102.5 | 19 | 9.1 | 5295 | 621 | 0.53 | 0.018673 |  | 1.418 |  | 2478 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00828009/FS | 3 | 110 | 09 | 5.1 | 2543 | 277 | 0.25 | 0.0064139 |  | 1.418 |  | 1190 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00828014/FS | 3 | 110 | 14 | 7.1 | 4152 | 452 | 0.42 | 0.016291 |  | 1.418 |  | 1943 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00828019/FS | 3 | 110 | 19 | 9.1 | 5701 | 621 | 0.57 | 0.021862 |  | 1.418 |  | 2668 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.00830009/FS | 3 | 118 | 09 | 5.1 | 2724 | 277 | 0.27 | 0.0076851 |  | 1.418 |  | 1275 | [19 empty] | 0.0001872 | 1.8444 | 1 | 0.0003432
Freestanding | Mini Freestanding | MINF.00830014/FS | 3 | 118 | 14 | 7.1 | 4449 | 452 | 0.44 | 0.018179 |  | 1.418 |  | 2082 | [19 empty] | 0.0001625 | 1.76 | 1 | 0.000403
Freestanding | Mini Freestanding | MINF.00830019/FS | 3 | 118 | 19 | 9.1 | 6109 | 621 | 0.61 | 0.025335 |  | 1.418 |  | 2859 | [19 empty] | 0.0001058 | 1.7486 | 1 | 0.0003162
Freestanding | Mini Freestanding | MINF.01306005/FS | 5 | 23.5 | 05 | 3.1 | 422 | 214 | 0.04 | 0.00026525 |  | 1.413 |  | 197 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01306010/FS | 5 | 23.5 | 10 | 5.1 | 647 | 329 | 0.06 | 0.00033294 |  | 1.419 |  | 303 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01306015/FS | 5 | 23.5 | 15 | 7.1 | 1086 | 552 | 0.11 | 0.001102 |  | 1.416 |  | 508 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01306020/FS | 5 | 23.5 | 20 | 9.1 | 1533 | 779 | 0.15 | 0.0015948 |  | 1.416 |  | 717 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01307005/FS | 5 | 27.5 | 05 | 3.1 | 492 | 214 | 0.05 | 0.00045148 |  | 1.413 |  | 230 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01307010/FS | 5 | 27.5 | 10 | 5.1 | 756 | 329 | 0.08 | 0.00061723 |  | 1.419 |  | 354 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01307015/FS | 5 | 27.5 | 15 | 7.1 | 1268 | 552 | 0.13 | 0.0015758 |  | 1.416 |  | 593 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01307020/FS | 5 | 27.5 | 20 | 9.1 | 1790 | 779 | 0.18 | 0.0023344 |  | 1.416 |  | 837 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01308005/FS | 5 | 31.5 | 05 | 3.1 | 563 | 215 | 0.06 | 0.00070157 |  | 1.413 |  | 263 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01308010/FS | 5 | 31.5 | 10 | 5.1 | 863 | 329 | 0.09 | 0.00082128 |  | 1.419 |  | 404 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01308015/FS | 5 | 31.5 | 15 | 7.1 | 1450 | 552 | 0.15 | 0.0021443 |  | 1.416 |  | 678 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01308020/FS | 5 | 31.5 | 20 | 9.1 | 2044 | 779 | 0.2 | 0.0029318 |  | 1.416 |  | 956 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01309005/FS | 5 | 35.5 | 05 | 3.1 | 634 | 215 | 0.06 | 0.00076727 |  | 1.413 |  | 296 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01309010/FS | 5 | 35.5 | 10 | 5.1 | 972 | 329 | 0.1 | 0.0010615 |  | 1.419 |  | 455 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01309015/FS | 5 | 35.5 | 15 | 7.1 | 1629 | 552 | 0.16 | 0.0024987 |  | 1.416 |  | 762 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01309020/FS | 5 | 35.5 | 20 | 9.1 | 2301 | 779 | 0.23 | 0.0039333 |  | 1.416 |  | 1076 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01310005/FS | 5 | 39.5 | 05 | 3.1 | 704 | 215 | 0.07 | 0.0011094 |  | 1.413 |  | 329 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01310010/FS | 5 | 39.5 | 10 | 5.1 | 1079 | 329 | 0.11 | 0.00134 |  | 1.419 |  | 505 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01310015/FS | 5 | 39.5 | 15 | 7.1 | 1811 | 552 | 0.18 | 0.0032237 |  | 1.416 |  | 847 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01310020/FS | 5 | 39.5 | 20 | 9.1 | 2555 | 779 | 0.26 | 0.0050954 |  | 1.416 |  | 1195 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01311005/FS | 5 | 43.5 | 05 | 3.1 | 775 | 215 | 0.08 | 0.0015321 |  | 1.413 |  | 362 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01311010/FS | 5 | 43.5 | 10 | 5.1 | 1188 | 329 | 0.12 | 0.0016589 |  | 1.419 |  | 556 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01311015/FS | 5 | 43.5 | 15 | 7.1 | 1993 | 552 | 0.2 | 0.0040531 |  | 1.416 |  | 932 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01311020/FS | 5 | 43.5 | 20 | 9.1 | 2812 | 779 | 0.28 | 0.0059968 |  | 1.416 |  | 1315 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01312005/FS | 5 | 47 | 05 | 3.1 | 845 | 215 | 0.08 | 0.0016421 |  | 1.413 |  | 395 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01312010/FS | 5 | 47 | 10 | 5.1 | 1295 | 329 | 0.13 | 0.0020201 |  | 1.419 |  | 606 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01312015/FS | 5 | 47 | 15 | 7.1 | 2172 | 552 | 0.22 | 0.0049904 |  | 1.416 |  | 1016 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01312020/FS | 5 | 47 | 20 | 9.1 | 3066 | 779 | 0.31 | 0.0074426 |  | 1.416 |  | 1434 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01314005/FS | 5 | 55 | 05 | 3.1 | 987 | 215 | 0.1 | 0.0028105 |  | 1.413 |  | 461 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01314010/FS | 5 | 55 | 10 | 5.1 | 1510 | 329 | 0.15 | 0.0028774 |  | 1.419 |  | 707 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01314015/FS | 5 | 55 | 15 | 7.1 | 2536 | 552 | 0.25 | 0.0066777 |  | 1.416 |  | 1186 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01314020/FS | 5 | 55 | 20 | 9.1 | 3577 | 779 | 0.36 | 0.010291 |  | 1.416 |  | 1673 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01316005/FS | 5 | 63 | 05 | 3.1 | 1126 | 215 | 0.11 | 0.0037401 |  | 1.413 |  | 526 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01316010/FS | 5 | 63 | 10 | 5.1 | 1726 | 329 | 0.17 | 0.0039271 |  | 1.419 |  | 808 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01316015/FS | 5 | 63 | 15 | 7.1 | 2897 | 552 | 0.29 | 0.0092599 |  | 1.416 |  | 1355 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01316020/FS | 5 | 63 | 20 | 9.1 | 4088 | 779 | 0.41 | 0.013664 |  | 1.416 |  | 1912 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01318005/FS | 5 | 71 | 05 | 3.1 | 1267 | 215 | 0.13 | 0.0056117 |  | 1.413 |  | 592 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01318010/FS | 5 | 71 | 10 | 5.1 | 1942 | 329 | 0.19 | 0.0051838 |  | 1.419 |  | 909 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01318015/FS | 5 | 71 | 15 | 7.1 | 3261 | 552 | 0.33 | 0.012333 |  | 1.416 |  | 1525 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01318020/FS | 5 | 71 | 20 | 9.1 | 4599 | 779 | 0.46 | 0.017582 |  | 1.416 |  | 2151 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01320005/FS | 5 | 78.5 | 05 | 3.1 | 1408 | 215 | 0.14 | 0.0070291 |  | 1.413 |  | 658 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01320010/FS | 5 | 78.5 | 10 | 5.1 | 2158 | 329 | 0.22 | 0.0072582 |  | 1.419 |  | 1010 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01320015/FS | 5 | 78.5 | 15 | 7.1 | 3622 | 552 | 0.36 | 0.015108 |  | 1.416 |  | 1694 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01320020/FS | 5 | 78.5 | 20 | 9.1 | 5110 | 779 | 0.51 | 0.022065 |  | 1.416 |  | 2390 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01322005/FS | 5 | 86.5 | 05 | 3.1 | 1550 | 215 | 0.16 | 0.0097405 |  | 1.413 |  | 724 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01322010/FS | 5 | 86.5 | 10 | 5.1 | 2373 | 329 | 0.24 | 0.009056 |  | 1.419 |  | 1111 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01322015/FS | 5 | 86.5 | 15 | 7.1 | 3984 | 552 | 0.4 | 0.019122 |  | 1.416 |  | 1863 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01322020/FS | 5 | 86.5 | 20 | 9.1 | 5621 | 779 | 0.56 | 0.027133 |  | 1.416 |  | 2629 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01324005/FS | 5 | 94.5 | 05 | 3.1 | 1691 | 215 | 0.17 | 0.011732 |  | 1.413 |  | 790 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01324010/FS | 5 | 94.5 | 10 | 5.1 | 2589 | 329 | 0.26 | 0.011106 |  | 1.419 |  | 1212 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01324015/FS | 5 | 94.5 | 15 | 7.1 | 4347 | 552 | 0.43 | 0.02268 |  | 1.416 |  | 2033 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01324020/FS | 5 | 94.5 | 20 | 9.1 | 6133 | 779 | 0.61 | 0.032806 |  | 1.416 |  | 2868 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01326005/FS | 5 | 102.5 | 05 | 3.1 | 1830 | 215 | 0.18 | 0.013963 |  | 1.413 |  | 855 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01326010/FS | 5 | 102.5 | 10 | 5.1 | 2805 | 329 | 0.28 | 0.013422 |  | 1.419 |  | 1313 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01326015/FS | 5 | 102.5 | 15 | 7.1 | 4708 | 552 | 0.47 | 0.027711 |  | 1.416 |  | 2202 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01326020/FS | 5 | 102.5 | 20 | 9.1 | 6644 | 779 | 0.66 | 0.039103 |  | 1.416 |  | 3107 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01328005/FS | 5 | 110 | 05 | 3.1 | 1971 | 215 | 0.2 | 0.018061 |  | 1.413 |  | 921 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01328010/FS | 5 | 110 | 10 | 5.1 | 3021 | 329 | 0.3 | 0.016015 |  | 1.419 |  | 1414 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01328015/FS | 5 | 110 | 15 | 7.1 | 5072 | 552 | 0.51 | 0.033338 |  | 1.416 |  | 2372 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01328020/FS | 5 | 110 | 20 | 9.1 | 7155 | 779 | 0.72 | 0.047292 |  | 1.416 |  | 3346 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.01330005/FS | 5 | 118 | 05 | 3.1 | 2113 | 215 | 0.21 | 0.02098 |  | 1.413 |  | 987 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Freestanding | Mini Freestanding | MINF.01330010/FS | 5 | 118 | 10 | 5.1 | 3236 | 329 | 0.32 | 0.018899 |  | 1.419 |  | 1515 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Freestanding | Mini Freestanding | MINF.01330015/FS | 5 | 118 | 15 | 7.1 | 5433 | 552 | 0.54 | 0.038233 |  | 1.416 |  | 2541 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Freestanding | Mini Freestanding | MINF.01330020/FS | 5 | 118 | 20 | 9.1 | 7666 | 779 | 0.77 | 0.054999 |  | 1.416 |  | 3585 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Freestanding | Mini Freestanding | MINF.02306006/FM | 9 | 23.5 | 06 | 3.1 | 692 | 352 | 0.07 | 0.001374 |  | 1.411 |  | 323 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02306011/FM | 9 | 23.5 | 11 | 5.1 | 1275 | 648 | 0.13 | 0.0024773 |  | 1.441 |  | 601 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02306016/FM | 9 | 23.5 | 16 | 7.1 | 1658 | 842 | 0.17 | 0.0074649 |  | 1.453 |  | 785 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02306021/FM | 9 | 23.5 | 21 | 9.1 | 2150 | 1092 | 0.22 | 0.004838 |  | 1.463 |  | 1021 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02307006/FM | 9 | 27.5 | 06 | 3.1 | 807 | 351 | 0.08 | 0.0019483 |  | 1.411 |  | 377 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02307011/FM | 9 | 27.5 | 11 | 5.1 | 1487 | 647 | 0.15 | 0.0034927 |  | 1.441 |  | 701 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02307016/FM | 9 | 27.5 | 16 | 7.1 | 1935 | 843 | 0.19 | 0.0094787 |  | 1.453 |  | 916 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02307021/FM | 9 | 27.5 | 21 | 9.1 | 2507 | 1092 | 0.25 | 0.0063935 |  | 1.463 |  | 1191 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02308006/FM | 9 | 31.5 | 06 | 3.1 | 923 | 352 | 0.09 | 0.0026398 |  | 1.411 |  | 431 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02308011/FM | 9 | 31.5 | 11 | 5.1 | 1701 | 648 | 0.17 | 0.0047246 |  | 1.441 |  | 802 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02308016/FM | 9 | 31.5 | 16 | 7.1 | 2209 | 842 | 0.22 | 0.012886 |  | 1.453 |  | 1046 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02308021/FM | 9 | 31.5 | 21 | 9.1 | 2865 | 1092 | 0.29 | 0.0087761 |  | 1.463 |  | 1361 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02309006/FM | 9 | 35.5 | 06 | 3.1 | 1039 | 352 | 0.1 | 0.003454 |  | 1.411 |  | 485 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02309011/FM | 9 | 35.5 | 11 | 5.1 | 1913 | 648 | 0.19 | 0.0061876 |  | 1.441 |  | 902 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02309016/FM | 9 | 35.5 | 16 | 7.1 | 2486 | 842 | 0.25 | 0.016861 |  | 1.453 |  | 1177 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02309021/FM | 9 | 35.5 | 21 | 9.1 | 3223 | 1092 | 0.32 | 0.010905 |  | 1.463 |  | 1531 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02310006/FM | 9 | 39.5 | 06 | 3.1 | 1154 | 352 | 0.12 | 0.0050362 |  | 1.411 |  | 539 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02310011/FM | 9 | 39.5 | 11 | 5.1 | 2125 | 648 | 0.21 | 0.0078961 |  | 1.441 |  | 1002 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02310016/FM | 9 | 39.5 | 16 | 7.1 | 2763 | 842 | 0.28 | 0.021416 |  | 1.453 |  | 1308 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02310021/FM | 9 | 39.5 | 21 | 9.1 | 3581 | 1091 | 0.36 | 0.014047 |  | 1.463 |  | 1701 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02311006/FM | 9 | 43.5 | 06 | 3.1 | 1270 | 352 | 0.13 | 0.0061961 |  | 1.411 |  | 593 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02311011/FM | 9 | 43.5 | 11 | 5.1 | 2337 | 648 | 0.23 | 0.0098638 |  | 1.441 |  | 1102 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02311016/FM | 9 | 43.5 | 16 | 7.1 | 3040 | 842 | 0.3 | 0.024914 |  | 1.453 |  | 1439 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02311021/FM | 9 | 43.5 | 21 | 9.1 | 3939 | 1091 | 0.39 | 0.016789 |  | 1.463 |  | 1871 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02312006/FM | 9 | 47 | 06 | 3.1 | 1386 | 352 | 0.14 | 0.007496 |  | 1.411 |  | 647 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02312011/FM | 9 | 47 | 11 | 5.1 | 2549 | 647 | 0.25 | 0.012104 |  | 1.441 |  | 1202 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02312016/FM | 9 | 47 | 16 | 7.1 | 3316 | 842 | 0.33 | 0.030493 |  | 1.453 |  | 1570 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02312021/FM | 9 | 47 | 21 | 9.1 | 4297 | 1091 | 0.43 | 0.020738 |  | 1.463 |  | 2041 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02314006/FM | 9 | 55 | 06 | 3.1 | 1617 | 352 | 0.16 | 0.010532 |  | 1.411 |  | 755 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02314011/FM | 9 | 55 | 11 | 5.1 | 2975 | 648 | 0.3 | 0.018591 |  | 1.441 |  | 1403 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02314016/FM | 9 | 55 | 16 | 7.1 | 3868 | 842 | 0.39 | 0.04352 |  | 1.453 |  | 1831 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02314021/FM | 9 | 55 | 21 | 9.1 | 5013 | 1091 | 0.5 | 0.028932 |  | 1.463 |  | 2381 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02316006/FM | 9 | 63 | 06 | 3.1 | 1846 | 352 | 0.18 | 0.014175 |  | 1.411 |  | 862 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02316011/FM | 9 | 63 | 11 | 5.1 | 3399 | 648 | 0.34 | 0.025417 |  | 1.441 |  | 1603 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02316016/FM | 9 | 63 | 16 | 7.1 | 4421 | 842 | 0.44 | 0.056597 |  | 1.453 |  | 2093 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02316021/FM | 9 | 63 | 21 | 9.1 | 5731 | 1092 | 0.57 | 0.03871 |  | 1.463 |  | 2722 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02318006/FM | 9 | 71 | 06 | 3.1 | 2078 | 352 | 0.21 | 0.019885 |  | 1.411 |  | 970 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02318011/FM | 9 | 71 | 11 | 5.1 | 3826 | 648 | 0.38 | 0.033602 |  | 1.441 |  | 1804 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02318016/FM | 9 | 71 | 16 | 7.1 | 4972 | 842 | 0.5 | 0.07449 |  | 1.453 |  | 2354 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02318021/FM | 9 | 71 | 21 | 9.1 | 6447 | 1092 | 0.64 | 0.050146 |  | 1.463 |  | 3062 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02320006/FM | 9 | 78.5 | 06 | 3.1 | 2309 | 352 | 0.23 | 0.025039 |  | 1.411 |  | 1078 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02320011/FM | 9 | 78.5 | 11 | 5.1 | 4250 | 648 | 0.43 | 0.045151 |  | 1.441 |  | 2004 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02320016/FM | 9 | 78.5 | 16 | 7.1 | 5526 | 842 | 0.55 | 0.091882 |  | 1.453 |  | 2616 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02320021/FM | 9 | 78.5 | 21 | 9.1 | 7162 | 1091 | 0.72 | 0.065033 |  | 1.463 |  | 3402 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02322006/FM | 9 | 86.5 | 06 | 3.1 | 2540 | 352 | 0.25 | 0.030889 |  | 1.411 |  | 1186 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02322011/FM | 9 | 86.5 | 11 | 5.1 | 4674 | 648 | 0.47 | 0.056608 |  | 1.441 |  | 2204 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02322016/FM | 9 | 86.5 | 16 | 7.1 | 6079 | 842 | 0.61 | 0.11498 |  | 1.453 |  | 2878 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02322021/FM | 9 | 86.5 | 21 | 9.1 | 7878 | 1091 | 0.79 | 0.080215 |  | 1.463 |  | 3742 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02324006/FM | 9 | 94.5 | 06 | 3.1 | 2771 | 352 | 0.28 | 0.039583 |  | 1.411 |  | 1294 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02324011/FM | 9 | 94.5 | 11 | 5.1 | 5100 | 648 | 0.51 | 0.069711 |  | 1.441 |  | 2405 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02324016/FM | 9 | 94.5 | 16 | 7.1 | 6631 | 842 | 0.66 | 0.13698 |  | 1.453 |  | 3139 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02324021/FM | 9 | 94.5 | 21 | 9.1 | 8594 | 1091 | 0.86 | 0.097276 |  | 1.463 |  | 4082 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02326006/FM | 9 | 102.5 | 06 | 3.1 | 3001 | 352 | 0.3 | 0.047127 |  | 1.411 |  | 1401 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02326011/FM | 9 | 102.5 | 11 | 5.1 | 5524 | 648 | 0.55 | 0.084547 |  | 1.441 |  | 2605 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02326016/FM | 9 | 102.5 | 16 | 7.1 | 7184 | 842 | 0.72 | 0.16561 |  | 1.453 |  | 3401 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02326021/FM | 9 | 102.5 | 21 | 9.1 | 9312 | 1092 | 0.93 | 0.11628 |  | 1.463 |  | 4423 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02328006/FM | 9 | 110 | 06 | 3.1 | 3232 | 352 | 0.32 | 0.05544 |  | 1.411 |  | 1509 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02328011/FM | 9 | 110 | 11 | 5.1 | 5951 | 648 | 0.6 | 0.10435 |  | 1.441 |  | 2806 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02328016/FM | 9 | 110 | 16 | 7.1 | 7735 | 842 | 0.77 | 0.1925 |  | 1.453 |  | 3662 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02328021/FM | 9 | 110 | 21 | 9.1 | 10028 | 1092 | 1 | 0.1373 |  | 1.463 |  | 4763 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02330006/FM | 9 | 118 | 06 | 3.1 | 3463 | 352 | 0.35 | 0.067429 |  | 1.411 |  | 1617 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02330011/FM | 9 | 118 | 11 | 5.1 | 6375 | 648 | 0.64 | 0.12323 |  | 1.441 |  | 3006 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02330016/FM | 9 | 118 | 16 | 7.1 | 8289 | 842 | 0.83 | 0.22696 |  | 1.453 |  | 3924 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02330021/FM | 9 | 118 | 21 | 9.1 | 10744 | 1092 | 1.07 | 0.1604 |  | 1.463 |  | 5103 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02806006/FM | 11 | 23.5 | 06 | 3.1 | 734 | 373 | 0.07 | 0.001374 |  | 1.403 |  | 342 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02806011/FM | 11 | 23.5 | 11 | 5.1 | 1385 | 704 | 0.14 | 0.0028541 |  | 1.441 |  | 653 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02806016/FM | 11 | 23.5 | 16 | 7.1 | 1815 | 922 | 0.18 | 0.0083571 |  | 1.455 |  | 860 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02806021/FM | 11 | 23.5 | 21 | 9.1 | 2370 | 1204 | 0.24 | 0.0057394 |  | 1.467 |  | 1127 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02807006/FM | 11 | 27.5 | 06 | 3.1 | 857 | 373 | 0.09 | 0.0023504 |  | 1.403 |  | 399 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02807011/FM | 11 | 27.5 | 11 | 5.1 | 1616 | 704 | 0.16 | 0.0039486 |  | 1.441 |  | 762 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02807016/FM | 11 | 27.5 | 16 | 7.1 | 2117 | 922 | 0.21 | 0.011546 |  | 1.455 |  | 1003 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02807021/FM | 11 | 27.5 | 21 | 9.1 | 2765 | 1204 | 0.28 | 0.0079822 |  | 1.467 |  | 1315 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02808006/FM | 11 | 31.5 | 06 | 3.1 | 979 | 373 | 0.1 | 0.0031181 |  | 1.403 |  | 456 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02808011/FM | 11 | 31.5 | 11 | 5.1 | 1847 | 704 | 0.18 | 0.0052643 |  | 1.441 |  | 871 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02808016/FM | 11 | 31.5 | 16 | 7.1 | 2419 | 922 | 0.24 | 0.015293 |  | 1.455 |  | 1146 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02808021/FM | 11 | 31.5 | 21 | 9.1 | 3160 | 1204 | 0.32 | 0.010637 |  | 1.467 |  | 1503 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02808111/DS/DBE | 11 | 32 | 11 | 5.1 | 2872 | 1081 | 0.29 | 0.013082 |  | 1 |  | 1171 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02808116/DS/DBE | 11 | 32 | 16 | 7.1 | 3989 | 1501 | 0.4 | 0.041902 |  | 1 |  | 1626 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02809006/FM | 11 | 35.5 | 06 | 3.1 | 1102 | 373 | 0.11 | 0.0040117 |  | 1.403 |  | 513 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02809011/FM | 11 | 35.5 | 11 | 5.1 | 2078 | 704 | 0.21 | 0.0074727 |  | 1.441 |  | 980 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02809016/FM | 11 | 35.5 | 16 | 7.1 | 2723 | 922 | 0.27 | 0.019613 |  | 1.455 |  | 1290 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02809021/FM | 11 | 35.5 | 21 | 9.1 | 3555 | 1204 | 0.36 | 0.013719 |  | 1.467 |  | 1691 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02810006/FM | 11 | 39.5 | 06 | 3.1 | 1224 | 373 | 0.12 | 0.0050362 |  | 1.403 |  | 570 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02810011/FM | 11 | 39.5 | 11 | 5.1 | 2309 | 704 | 0.23 | 0.009368 |  | 1.441 |  | 1089 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02810016/FM | 11 | 39.5 | 16 | 7.1 | 3025 | 922 | 0.3 | 0.02452 |  | 1.455 |  | 1433 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02810021/FM | 11 | 39.5 | 21 | 9.1 | 3951 | 1204 | 0.4 | 0.017241 |  | 1.467 |  | 1879 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02810111/DS/DBE | 11 | 40 | 11 | 5.1 | 4143 | 1250 | 0.41 | 0.027986 |  | 1 |  | 1689 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02810116/DS/DBE | 11 | 40 | 16 | 7.1 | 5870 | 1771 | 0.59 | 0.09274 |  | 1 |  | 2393 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02811006/FM | 11 | 43.5 | 06 | 3.1 | 1346 | 373 | 0.13 | 0.0061961 |  | 1.403 |  | 627 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02811011/FM | 11 | 43.5 | 11 | 5.1 | 2541 | 704 | 0.25 | 0.011531 |  | 1.441 |  | 1198 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02811016/FM | 11 | 43.5 | 16 | 7.1 | 3327 | 922 | 0.33 | 0.030028 |  | 1.455 |  | 1576 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02811021/FM | 11 | 43.5 | 21 | 9.1 | 4346 | 1204 | 0.43 | 0.020292 |  | 1.467 |  | 2067 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02812006/FM | 11 | 47 | 06 | 3.1 | 1469 | 373 | 0.15 | 0.0083446 |  | 1.403 |  | 684 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02812011/FM | 11 | 47 | 11 | 5.1 | 2772 | 704 | 0.28 | 0.014959 |  | 1.441 |  | 1307 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02812016/FM | 11 | 47 | 16 | 7.1 | 3631 | 922 | 0.36 | 0.03615 |  | 1.455 |  | 1720 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02812021/FM | 11 | 47 | 21 | 9.1 | 4741 | 1204 | 0.47 | 0.024638 |  | 1.467 |  | 2255 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02812111/DS/DBE | 11 | 47.5 | 11 | 5.1 | 4678 | 1178 | 0.47 | 0.039654 |  | 1 |  | 1907 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02812116/DS/DBE | 11 | 47.5 | 16 | 7.1 | 6574 | 1656 | 0.66 | 0.1187 |  | 1 |  | 2680 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02814006/FM | 11 | 55 | 06 | 3.1 | 1714 | 373 | 0.17 | 0.011566 |  | 1.403 |  | 798 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02814011/FM | 11 | 55 | 11 | 5.1 | 3234 | 704 | 0.32 | 0.020961 |  | 1.441 |  | 1525 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02814016/FM | 11 | 55 | 16 | 7.1 | 4235 | 922 | 0.42 | 0.05029 |  | 1.455 |  | 2006 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02814021/FM | 11 | 55 | 21 | 9.1 | 5532 | 1204 | 0.55 | 0.034779 |  | 1.467 |  | 2631 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02814111/DS/DBE | 11 | 55.5 | 11 | 5.1 | 5948 | 1286 | 0.59 | 0.065884 |  | 1 |  | 2425 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02814116/DS/DBE | 11 | 55.5 | 16 | 7.1 | 8453 | 1827 | 0.85 | 0.19981 |  | 1 |  | 3446 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02816006/FM | 11 | 63 | 06 | 3.1 | 1958 | 373 | 0.2 | 0.016668 |  | 1.403 |  | 912 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02816011/FM | 11 | 63 | 11 | 5.1 | 3694 | 704 | 0.37 | 0.029727 |  | 1.441 |  | 1742 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02816016/FM | 11 | 63 | 16 | 7.1 | 4840 | 922 | 0.48 | 0.067041 |  | 1.455 |  | 2293 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02816021/FM | 11 | 63 | 21 | 9.1 | 6320 | 1204 | 0.63 | 0.046935 |  | 1.467 |  | 3006 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02818006/FM | 11 | 71 | 06 | 3.1 | 2203 | 373 | 0.22 | 0.021355 |  | 1.403 |  | 1026 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02818011/FM | 11 | 71 | 11 | 5.1 | 4157 | 704 | 0.42 | 0.04042 |  | 1.441 |  | 1960 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02818016/FM | 11 | 71 | 16 | 7.1 | 5444 | 922 | 0.54 | 0.086499 |  | 1.455 |  | 2579 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02818021/FM | 11 | 71 | 21 | 9.1 | 7111 | 1204 | 0.71 | 0.061204 |  | 1.467 |  | 3382 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02818111/DS/DBE | 11 | 71.5 | 11 | 5.1 | 7751 | 1305 | 0.78 | 0.12763 |  | 1 |  | 3160 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02818116/DS/DBE | 11 | 71.5 | 16 | 7.1 | 11036 | 1858 | 1.1 | 0.34599 |  | 1 |  | 4499 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02820006/FM | 11 | 78.5 | 06 | 3.1 | 2448 | 373 | 0.24 | 0.02672 |  | 1.403 |  | 1140 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02820011/FM | 11 | 78.5 | 11 | 5.1 | 4619 | 704 | 0.46 | 0.051118 |  | 1.441 |  | 2178 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02820016/FM | 11 | 78.5 | 16 | 7.1 | 6050 | 922 | 0.61 | 0.1123 |  | 1.455 |  | 2866 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02820021/FM | 11 | 78.5 | 21 | 9.1 | 7901 | 1204 | 0.79 | 0.077678 |  | 1.467 |  | 3758 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02822006/FM | 11 | 86.5 | 06 | 3.1 | 2693 | 373 | 0.27 | 0.034729 |  | 1.403 |  | 1254 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02822011/FM | 11 | 86.5 | 11 | 5.1 | 5081 | 704 | 0.51 | 0.065765 |  | 1.441 |  | 2396 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02822016/FM | 11 | 86.5 | 16 | 7.1 | 6656 | 922 | 0.67 | 0.13786 |  | 1.455 |  | 3153 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02822021/FM | 11 | 86.5 | 21 | 9.1 | 8692 | 1204 | 0.87 | 0.096447 |  | 1.467 |  | 4134 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02824006/FM | 11 | 94.5 | 06 | 3.1 | 2938 | 373 | 0.29 | 0.041751 |  | 1.403 |  | 1368 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02824011/FM | 11 | 94.5 | 11 | 5.1 | 5543 | 704 | 0.55 | 0.080048 |  | 1.441 |  | 2614 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02824016/FM | 11 | 94.5 | 16 | 7.1 | 7259 | 922 | 0.73 | 0.16642 |  | 1.455 |  | 3439 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02824021/FM | 11 | 94.5 | 21 | 9.1 | 9483 | 1204 | 0.95 | 0.1176 |  | 1.467 |  | 4510 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02824111/DS/DBE | 11 | 95 | 11 | 5.1 | 10827 | 1369 | 1.08 | 0.27729 |  | 1 |  | 4414 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02824116/DS/DBE | 11 | 95 | 16 | 7.1 | 15500 | 1960 | 1.55 | 0.71606 |  | 1 |  | 6319 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02826006/FM | 11 | 102.5 | 06 | 3.1 | 3183 | 373 | 0.32 | 0.051971 |  | 1.403 |  | 1482 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02826011/FM | 11 | 102.5 | 11 | 5.1 | 6004 | 704 | 0.6 | 0.099116 |  | 1.441 |  | 2831 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02826016/FM | 11 | 102.5 | 16 | 7.1 | 7865 | 922 | 0.79 | 0.19804 |  | 1.455 |  | 3726 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02826021/FM | 11 | 102.5 | 21 | 9.1 | 10271 | 1204 | 1.03 | 0.14122 |  | 1.467 |  | 4885 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02828006/FM | 11 | 110 | 06 | 3.1 | 3427 | 373 | 0.34 | 0.060764 |  | 1.403 |  | 1596 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02828011/FM | 11 | 110 | 11 | 5.1 | 6466 | 704 | 0.65 | 0.12075 |  | 1.441 |  | 3049 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02828016/FM | 11 | 110 | 16 | 7.1 | 8469 | 922 | 0.85 | 0.23283 |  | 1.455 |  | 4012 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02828021/FM | 11 | 110 | 21 | 9.1 | 11062 | 1204 | 1.11 | 0.16739 |  | 1.467 |  | 5261 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Freestanding | Mini Freestanding | MINF.02830006/FM | 11 | 118 | 06 | 3.1 | 3672 | 373 | 0.37 | 0.073334 |  | 1.403 |  | 1710 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Freestanding | Mini Freestanding | MINF.02830011/FM | 11 | 118 | 11 | 5.1 | 6928 | 704 | 0.69 | 0.14132 |  | 1.441 |  | 3267 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Freestanding | Mini Freestanding | MINF.02830016/FM | 11 | 118 | 16 | 7.1 | 9075 | 922 | 0.91 | 0.27085 |  | 1.455 |  | 4299 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Freestanding | Mini Freestanding | MINF.02830021/FM | 11 | 118 | 21 | 9.1 | 11852 | 1204 | 1.19 | 0.19619 |  | 1.467 |  | 5637 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.02005006 | 8 | 19.5 | 06 | 3.3 | 576 | 351 | 0.06 | 0.00091073 |  | 1.41 |  | 269 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02005010 | 8 | 19.5 | 10 | 4.6 | 702 | 428 | 0.07 | 0.00041569 |  | 1.413 |  | 328 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02005015 | 8 | 19.5 | 15 | 6.6 | 1168 | 712 | 0.12 | 0.0012664 |  | 1.408 |  | 545 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02005020 | 8 | 19.5 | 20 | 8.6 | 1642 | 1001 | 0.16 | 0.0017706 |  | 1.408 |  | 766 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02006006 | 8 | 23.5 | 06 | 3.3 | 692 | 352 | 0.07 | 0.001374 |  | 1.41 |  | 323 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02006010 | 8 | 23.5 | 10 | 4.6 | 841 | 427 | 0.08 | 0.00057754 |  | 1.413 |  | 393 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02006015 | 8 | 23.5 | 15 | 6.6 | 1402 | 712 | 0.14 | 0.0017685 |  | 1.408 |  | 654 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02006020 | 8 | 23.5 | 20 | 8.6 | 1970 | 1001 | 0.2 | 0.0028126 |  | 1.408 |  | 919 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02007006 | 8 | 27.5 | 06 | 3.3 | 808 | 352 | 0.08 | 0.0019483 |  | 1.41 |  | 377 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02007010 | 8 | 27.5 | 10 | 4.6 | 982 | 428 | 0.1 | 0.0009446 |  | 1.413 |  | 459 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02007015 | 8 | 27.5 | 15 | 6.6 | 1636 | 712 | 0.16 | 0.0023652 |  | 1.408 |  | 763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02007020 | 8 | 27.5 | 20 | 8.6 | 2298 | 1001 | 0.23 | 0.0037818 |  | 1.408 |  | 1072 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02008006 | 8 | 31.5 | 06 | 3.3 | 921 | 351 | 0.09 | 0.0026398 |  | 1.41 |  | 430 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02008010 | 8 | 31.5 | 10 | 4.6 | 1122 | 427 | 0.11 | 0.0012021 |  | 1.413 |  | 524 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02008015 | 8 | 31.5 | 15 | 6.6 | 1869 | 712 | 0.19 | 0.0034008 |  | 1.408 |  | 872 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02008020 | 8 | 31.5 | 20 | 8.6 | 2628 | 1001 | 0.26 | 0.0049082 |  | 1.408 |  | 1226 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02009006 | 8 | 35.5 | 06 | 3.3 | 1037 | 351 | 0.1 | 0.003454 |  | 1.41 |  | 484 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02009010 | 8 | 35.5 | 10 | 4.6 | 1263 | 428 | 0.13 | 0.0017437 |  | 1.413 |  | 590 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02009015 | 8 | 35.5 | 15 | 6.6 | 2103 | 712 | 0.21 | 0.0042415 |  | 1.408 |  | 981 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02009020 | 8 | 35.5 | 20 | 8.6 | 2956 | 1001 | 0.3 | 0.0066224 |  | 1.408 |  | 1379 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02010006 | 8 | 39.5 | 06 | 3.3 | 1153 | 351 | 0.12 | 0.0050362 |  | 1.41 |  | 538 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02010010 | 8 | 39.5 | 10 | 4.6 | 1402 | 427 | 0.14 | 0.0021113 |  | 1.413 |  | 655 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02010015 | 8 | 39.5 | 15 | 6.6 | 2337 | 712 | 0.23 | 0.0051886 |  | 1.408 |  | 1090 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02010020 | 8 | 39.5 | 20 | 8.6 | 3284 | 1001 | 0.33 | 0.0081256 |  | 1.408 |  | 1532 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02011006 | 8 | 43.5 | 06 | 3.3 | 1268 | 351 | 0.13 | 0.0061961 |  | 1.41 |  | 592 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02011010 | 8 | 43.5 | 10 | 4.6 | 1543 | 428 | 0.15 | 0.0025231 |  | 1.413 |  | 721 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02011015 | 8 | 43.5 | 15 | 6.6 | 2571 | 712 | 0.26 | 0.0067392 |  | 1.408 |  | 1199 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02011020 | 8 | 43.5 | 20 | 8.6 | 3613 | 1001 | 0.36 | 0.0097997 |  | 1.408 |  | 1685 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02012006 | 8 | 47 | 06 | 3.3 | 1384 | 352 | 0.14 | 0.007496 |  | 1.41 |  | 646 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02012010 | 8 | 47 | 10 | 4.6 | 1682 | 427 | 0.17 | 0.0033402 |  | 1.413 |  | 786 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02012015 | 8 | 47 | 15 | 6.6 | 2804 | 712 | 0.28 | 0.0079564 |  | 1.408 |  | 1308 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02012020 | 8 | 47 | 20 | 8.6 | 3941 | 1001 | 0.39 | 0.011649 |  | 1.408 |  | 1838 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02014006 | 8 | 55 | 06 | 3.3 | 1613 | 351 | 0.16 | 0.010532 |  | 1.41 |  | 753 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02014010 | 8 | 55 | 10 | 4.6 | 1963 | 427 | 0.2 | 0.0049216 |  | 1.413 |  | 917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02014015 | 8 | 55 | 15 | 6.6 | 3272 | 712 | 0.33 | 0.011403 |  | 1.408 |  | 1526 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02014020 | 8 | 55 | 20 | 8.6 | 4599 | 1001 | 0.46 | 0.016582 |  | 1.408 |  | 2145 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02016006 | 8 | 63 | 06 | 3.3 | 1845 | 351 | 0.18 | 0.014175 |  | 1.41 |  | 861 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02016010 | 8 | 63 | 10 | 4.6 | 2243 | 427 | 0.22 | 0.0063403 |  | 1.413 |  | 1048 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02016015 | 8 | 63 | 15 | 6.6 | 3739 | 712 | 0.37 | 0.014787 |  | 1.408 |  | 1744 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02016020 | 8 | 63 | 20 | 8.6 | 5255 | 1001 | 0.53 | 0.022489 |  | 1.408 |  | 2451 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02018006 | 8 | 71 | 06 | 3.3 | 2074 | 351 | 0.21 | 0.019885 |  | 1.41 |  | 968 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02018010 | 8 | 71 | 10 | 4.6 | 2524 | 427 | 0.25 | 0.0086163 |  | 1.413 |  | 1179 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02018015 | 8 | 71 | 15 | 6.6 | 4206 | 712 | 0.42 | 0.019575 |  | 1.408 |  | 1962 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02018020 | 8 | 71 | 20 | 8.6 | 5913 | 1001 | 0.59 | 0.028468 |  | 1.408 |  | 2758 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02020006 | 8 | 78.5 | 06 | 3.3 | 2305 | 351 | 0.23 | 0.025039 |  | 1.41 |  | 1076 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02020010 | 8 | 78.5 | 10 | 4.6 | 2804 | 427 | 0.28 | 0.011329 |  | 1.413 |  | 1310 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02020015 | 8 | 78.5 | 15 | 6.6 | 4674 | 712 | 0.47 | 0.025145 |  | 1.408 |  | 2180 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02020020 | 8 | 78.5 | 20 | 8.6 | 6569 | 1001 | 0.66 | 0.03631 |  | 1.408 |  | 3064 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02024006 | 8 | 94.5 | 06 | 3.3 | 2766 | 351 | 0.28 | 0.039583 |  | 1.41 |  | 1291 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02024010 | 8 | 94.5 | 10 | 4.6 | 3365 | 427 | 0.34 | 0.018179 |  | 1.413 |  | 1572 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02024015 | 8 | 94.5 | 15 | 6.6 | 5608 | 712 | 0.56 | 0.03748 |  | 1.408 |  | 2616 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02024020 | 8 | 94.5 | 20 | 8.6 | 7883 | 1001 | 0.79 | 0.053957 |  | 1.408 |  | 3677 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.02028006 | 8 | 110 | 06 | 3.3 | 3227 | 351 | 0.32 | 0.05544 |  | 1.41 |  | 1506 | [19 empty] | 0.0041689 | 1.4116 | 3 | 0.00054247
Horizontal Wall | Strada | STRW.02028010 | 8 | 110 | 10 | 4.6 | 3925 | 427 | 0.39 | 0.025879 |  | 1.413 |  | 1834 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.02028015 | 8 | 110 | 15 | 6.6 | 6543 | 712 | 0.65 | 0.052778 |  | 1.408 |  | 3052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.02028020 | 8 | 110 | 20 | 8.6 | 9197 | 1001 | 0.92 | 0.07567 |  | 1.408 |  | 4290 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03505006 | 14 | 19.5 | 06 | 3.3 | 851 | 519 | 0.09 | 0.0023885 |  | 1.393 |  | 395 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03505010 | 14 | 19.5 | 10 | 4.6 | 965 | 588 | 0.1 | 0.00082769 |  | 1.399 |  | 449 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03505011 | 14 | 19.5 | 11 | 4.6 | 1269 | 774 | 0.13 | 0.0022931 |  | 1.44 |  | 598 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03505015 | 14 | 19.5 | 15 | 6.6 | 1585 | 966 | 0.16 | 0.0022317 |  | 1.39 |  | 735 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03505016 | 14 | 19.5 | 16 | 6.6 | 1681 | 1025 | 0.17 | 0.0073168 |  | 1.458 |  | 797 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03505020 | 14 | 19.5 | 20 | 8.6 | 2221 | 1354 | 0.22 | 0.0033244 |  | 1.39 |  | 1030 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03505021 | 14 | 19.5 | 21 | 8.6 | 2219 | 1353 | 0.22 | 0.0046976 |  | 1.472 |  | 1057 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03506006 | 14 | 23.5 | 06 | 3.3 | 1021 | 519 | 0.1 | 0.0031296 |  | 1.393 |  | 474 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03506010 | 14 | 23.5 | 10 | 4.6 | 1159 | 589 | 0.12 | 0.0012579 |  | 1.399 |  | 539 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03506011 | 14 | 23.5 | 11 | 4.6 | 1523 | 774 | 0.15 | 0.0032565 |  | 1.44 |  | 718 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03506015 | 14 | 23.5 | 15 | 6.6 | 1902 | 966 | 0.19 | 0.0032213 |  | 1.39 |  | 882 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03506016 | 14 | 23.5 | 16 | 6.6 | 2016 | 1024 | 0.2 | 0.010291 |  | 1.458 |  | 956 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03506020 | 14 | 23.5 | 20 | 8.6 | 2666 | 1354 | 0.27 | 0.0050863 |  | 1.39 |  | 1236 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03506021 | 14 | 23.5 | 21 | 8.6 | 2662 | 1352 | 0.27 | 0.0072336 |  | 1.472 |  | 1268 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03507006 | 14 | 27.5 | 06 | 3.3 | 1191 | 519 | 0.12 | 0.0047907 |  | 1.393 |  | 553 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03507010 | 14 | 27.5 | 10 | 4.6 | 1353 | 589 | 0.14 | 0.001797 |  | 1.399 |  | 629 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03507011 | 14 | 27.5 | 11 | 4.6 | 1776 | 773 | 0.18 | 0.0049402 |  | 1.44 |  | 837 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03507015 | 14 | 27.5 | 15 | 6.6 | 2219 | 966 | 0.22 | 0.0044127 |  | 1.39 |  | 1029 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03507016 | 14 | 27.5 | 16 | 6.6 | 2351 | 1024 | 0.24 | 0.015024 |  | 1.458 |  | 1115 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03507020 | 14 | 27.5 | 20 | 8.6 | 3110 | 1354 | 0.31 | 0.0068091 |  | 1.39 |  | 1442 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03507021 | 14 | 27.5 | 21 | 8.6 | 3107 | 1353 | 0.31 | 0.0097438 |  | 1.472 |  | 1480 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03508006 | 14 | 31.5 | 06 | 3.3 | 1362 | 519 | 0.14 | 0.0069176 |  | 1.393 |  | 632 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03508010 | 14 | 31.5 | 10 | 4.6 | 1544 | 588 | 0.15 | 0.0021688 |  | 1.399 |  | 718 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03508011 | 14 | 31.5 | 11 | 4.6 | 2030 | 773 | 0.2 | 0.0064267 |  | 1.44 |  | 957 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03508015 | 14 | 31.5 | 15 | 6.6 | 2536 | 966 | 0.25 | 0.0058134 |  | 1.39 |  | 1176 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03508016 | 14 | 31.5 | 16 | 6.6 | 2687 | 1024 | 0.27 | 0.019284 |  | 1.458 |  | 1274 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03508020 | 14 | 31.5 | 20 | 8.6 | 3554 | 1354 | 0.36 | 0.0093079 |  | 1.39 |  | 1648 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03508021 | 14 | 31.5 | 21 | 8.6 | 3550 | 1353 | 0.36 | 0.013391 |  | 1.472 |  | 1691 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03509006 | 14 | 35.5 | 06 | 3.3 | 1532 | 519 | 0.15 | 0.0083775 |  | 1.393 |  | 711 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03509010 | 14 | 35.5 | 10 | 4.6 | 1737 | 588 | 0.17 | 0.0029 |  | 1.399 |  | 808 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03509011 | 14 | 35.5 | 11 | 4.6 | 2283 | 773 | 0.23 | 0.0088722 |  | 1.44 |  | 1076 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03509015 | 14 | 35.5 | 15 | 6.6 | 2853 | 966 | 0.29 | 0.0079576 |  | 1.39 |  | 1323 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03509016 | 14 | 35.5 | 16 | 6.6 | 3024 | 1024 | 0.3 | 0.024125 |  | 1.458 |  | 1434 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03509020 | 14 | 35.5 | 20 | 8.6 | 3999 | 1354 | 0.4 | 0.011649 |  | 1.39 |  | 1854 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03509021 | 14 | 35.5 | 21 | 8.6 | 3995 | 1353 | 0.4 | 0.016848 |  | 1.472 |  | 1903 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03510006 | 14 | 39.5 | 06 | 3.3 | 1702 | 519 | 0.17 | 0.011369 |  | 1.393 |  | 790 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03510010 | 14 | 39.5 | 10 | 4.6 | 1931 | 589 | 0.19 | 0.0037601 |  | 1.399 |  | 898 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03510011 | 14 | 39.5 | 11 | 4.6 | 2537 | 773 | 0.25 | 0.010958 |  | 1.44 |  | 1196 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03510015 | 14 | 39.5 | 15 | 6.6 | 3170 | 966 | 0.32 | 0.0098637 |  | 1.39 |  | 1470 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03510016 | 14 | 39.5 | 16 | 6.6 | 3359 | 1024 | 0.34 | 0.031347 |  | 1.458 |  | 1593 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03510020 | 14 | 39.5 | 20 | 8.6 | 4443 | 1354 | 0.44 | 0.01428 |  | 1.39 |  | 2060 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03510021 | 14 | 39.5 | 21 | 8.6 | 4438 | 1353 | 0.44 | 0.020756 |  | 1.472 |  | 2114 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03511006 | 14 | 43.5 | 06 | 3.3 | 1872 | 519 | 0.19 | 0.014976 |  | 1.393 |  | 869 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03511010 | 14 | 43.5 | 10 | 4.6 | 2124 | 589 | 0.21 | 0.0047563 |  | 1.399 |  | 988 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03511011 | 14 | 43.5 | 11 | 4.6 | 2792 | 774 | 0.28 | 0.014261 |  | 1.44 |  | 1316 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03511015 | 14 | 43.5 | 15 | 6.6 | 3487 | 966 | 0.35 | 0.012002 |  | 1.39 |  | 1617 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03511016 | 14 | 43.5 | 16 | 6.6 | 3695 | 1024 | 0.37 | 0.037575 |  | 1.458 |  | 1752 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03511020 | 14 | 43.5 | 20 | 8.6 | 4887 | 1354 | 0.49 | 0.017917 |  | 1.39 |  | 2266 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03511021 | 14 | 43.5 | 21 | 8.6 | 4880 | 1352 | 0.49 | 0.026153 |  | 1.472 |  | 2325 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03512006 | 14 | 47 | 06 | 3.3 | 2043 | 519 | 0.2 | 0.017407 |  | 1.393 |  | 948 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03512010 | 14 | 47 | 10 | 4.6 | 2318 | 589 | 0.23 | 0.0058954 |  | 1.399 |  | 1078 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03512011 | 14 | 47 | 11 | 4.6 | 3044 | 773 | 0.3 | 0.017018 |  | 1.44 |  | 1435 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03512015 | 14 | 47 | 15 | 6.6 | 3804 | 966 | 0.38 | 0.014379 |  | 1.39 |  | 1764 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03512016 | 14 | 47 | 16 | 6.6 | 4032 | 1024 | 0.4 | 0.044428 |  | 1.458 |  | 1912 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03512020 | 14 | 47 | 20 | 8.6 | 5331 | 1354 | 0.53 | 0.021213 |  | 1.39 |  | 2472 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03512021 | 14 | 47 | 21 | 8.6 | 5325 | 1353 | 0.53 | 0.031101 |  | 1.472 |  | 2537 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03514006 | 14 | 55 | 06 | 3.3 | 2383 | 519 | 0.24 | 0.027623 |  | 1.393 |  | 1106 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03514010 | 14 | 55 | 10 | 4.6 | 2703 | 588 | 0.27 | 0.0086287 |  | 1.399 |  | 1257 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03514011 | 14 | 55 | 11 | 4.6 | 3551 | 773 | 0.36 | 0.026099 |  | 1.44 |  | 1674 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03514015 | 14 | 55 | 15 | 6.6 | 4438 | 966 | 0.44 | 0.019875 |  | 1.39 |  | 2058 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03514016 | 14 | 55 | 16 | 6.6 | 4703 | 1024 | 0.47 | 0.062638 |  | 1.458 |  | 2230 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03514020 | 14 | 55 | 20 | 8.6 | 6220 | 1354 | 0.62 | 0.029668 |  | 1.39 |  | 2884 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03514021 | 14 | 55 | 21 | 8.6 | 6213 | 1353 | 0.62 | 0.043839 |  | 1.472 |  | 2960 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03516006 | 14 | 63 | 06 | 3.3 | 2723 | 519 | 0.27 | 0.038161 |  | 1.393 |  | 1264 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03516010 | 14 | 63 | 10 | 4.6 | 3090 | 589 | 0.31 | 0.012012 |  | 1.399 |  | 1437 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03516011 | 14 | 63 | 11 | 4.6 | 4060 | 773 | 0.41 | 0.035959 |  | 1.44 |  | 1914 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03516015 | 14 | 63 | 15 | 6.6 | 5073 | 966 | 0.51 | 0.02743 |  | 1.39 |  | 2352 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03516016 | 14 | 63 | 16 | 6.6 | 5375 | 1024 | 0.54 | 0.084326 |  | 1.458 |  | 2549 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03516020 | 14 | 63 | 20 | 8.6 | 7108 | 1354 | 0.71 | 0.039708 |  | 1.39 |  | 3296 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03516021 | 14 | 63 | 21 | 8.6 | 7099 | 1352 | 0.71 | 0.059092 |  | 1.472 |  | 3382 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03518006 | 14 | 71 | 06 | 3.3 | 3064 | 519 | 0.31 | 0.054759 |  | 1.393 |  | 1422 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03518010 | 14 | 71 | 10 | 4.6 | 3475 | 588 | 0.35 | 0.016094 |  | 1.399 |  | 1616 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03518011 | 14 | 71 | 11 | 4.6 | 4567 | 773 | 0.46 | 0.047819 |  | 1.44 |  | 2153 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03518015 | 14 | 71 | 15 | 6.6 | 5707 | 966 | 0.57 | 0.035186 |  | 1.39 |  | 2646 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03518016 | 14 | 71 | 16 | 6.6 | 6046 | 1024 | 0.6 | 0.10615 |  | 1.458 |  | 2867 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03518020 | 14 | 71 | 20 | 8.6 | 7997 | 1354 | 0.8 | 0.051391 |  | 1.39 |  | 3708 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03518021 | 14 | 71 | 21 | 8.6 | 7987 | 1352 | 0.8 | 0.076979 |  | 1.472 |  | 3805 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03520006 | 14 | 78.5 | 06 | 3.3 | 3404 | 519 | 0.34 | 0.071138 |  | 1.393 |  | 1580 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03520010 | 14 | 78.5 | 10 | 4.6 | 3862 | 589 | 0.39 | 0.020923 |  | 1.399 |  | 1796 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03520011 | 14 | 78.5 | 11 | 4.6 | 5074 | 773 | 0.51 | 0.061818 |  | 1.44 |  | 2392 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03520015 | 14 | 78.5 | 15 | 6.6 | 6341 | 966 | 0.63 | 0.044072 |  | 1.39 |  | 2940 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03520016 | 14 | 78.5 | 16 | 6.6 | 6719 | 1024 | 0.67 | 0.13471 |  | 1.458 |  | 3186 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03520020 | 14 | 78.5 | 20 | 8.6 | 8886 | 1354 | 0.89 | 0.064774 |  | 1.39 |  | 4120 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03520021 | 14 | 78.5 | 21 | 8.6 | 8875 | 1353 | 0.89 | 0.097613 |  | 1.472 |  | 4228 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03524006 | 14 | 94.5 | 06 | 3.3 | 4085 | 519 | 0.41 | 0.11939 |  | 1.393 |  | 1896 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03524010 | 14 | 94.5 | 10 | 4.6 | 4634 | 589 | 0.46 | 0.031721 |  | 1.399 |  | 2155 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03524011 | 14 | 94.5 | 11 | 4.6 | 6088 | 773 | 0.61 | 0.096773 |  | 1.44 |  | 2870 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03524015 | 14 | 94.5 | 15 | 6.6 | 7609 | 966 | 0.76 | 0.067088 |  | 1.39 |  | 3528 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03524016 | 14 | 94.5 | 16 | 6.6 | 8062 | 1024 | 0.81 | 0.20345 |  | 1.458 |  | 3823 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03524020 | 14 | 94.5 | 20 | 8.6 | 10663 | 1354 | 1.07 | 0.096859 |  | 1.39 |  | 4944 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03524021 | 14 | 94.5 | 21 | 8.6 | 10651 | 1353 | 1.07 | 0.14756 |  | 1.472 |  | 5074 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.03528006 | 14 | 110 | 06 | 3.3 | 4766 | 519 | 0.48 | 0.18606 |  | 1.393 |  | 2212 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.03528010 | 14 | 110 | 10 | 4.6 | 5406 | 588 | 0.54 | 0.047004 |  | 1.399 |  | 2514 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.03528011 | 14 | 110 | 11 | 4.6 | 7105 | 773 | 0.71 | 0.14187 |  | 1.44 |  | 3349 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.03528015 | 14 | 110 | 15 | 6.6 | 8877 | 966 | 0.89 | 0.095853 |  | 1.39 |  | 4116 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.03528016 | 14 | 110 | 16 | 6.6 | 9405 | 1024 | 0.94 | 0.28263 |  | 1.458 |  | 4460 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.03528020 | 14 | 110 | 20 | 8.6 | 12440 | 1354 | 1.24 | 0.13429 |  | 1.39 |  | 5768 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.03528021 | 14 | 110 | 21 | 8.6 | 12425 | 1353 | 1.24 | 0.2066 |  | 1.472 |  | 5919 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05005006 | 19.5 | 19.5 | 06 | 3.3 | 1028 | 627 | 0.1 | 0.0029581 |  | 1.372 |  | 474 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05005010 | 19.5 | 19.5 | 10 | 4.6 | 1162 | 708 | 0.12 | 0.0011777 |  | 1.385 |  | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05005011 | 19.5 | 19.5 | 11 | 4.6 | 1471 | 897 | 0.15 | 0.0030203 |  | 1.438 |  | 693 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05005015 | 19.5 | 19.5 | 15 | 6.6 | 1880 | 1146 | 0.19 | 0.0031316 |  | 1.373 |  | 867 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05005016 | 19.5 | 19.5 | 16 | 6.6 | 1997 | 1217 | 0.2 | 0.010095 |  | 1.464 |  | 949 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05005020 | 19.5 | 19.5 | 20 | 8.6 | 2631 | 1604 | 0.26 | 0.0046274 |  | 1.373 |  | 1213 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05005021 | 19.5 | 19.5 | 21 | 8.6 | 2698 | 1645 | 0.27 | 0.0070338 |  | 1.485 |  | 1291 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05006006 | 19.5 | 23.5 | 06 | 3.3 | 1232 | 626 | 0.12 | 0.004537 |  | 1.372 |  | 568 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05006010 | 19.5 | 23.5 | 10 | 4.6 | 1396 | 709 | 0.14 | 0.0016922 |  | 1.385 |  | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05006011 | 19.5 | 23.5 | 11 | 4.6 | 1766 | 897 | 0.18 | 0.0046161 |  | 1.438 |  | 832 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05006015 | 19.5 | 23.5 | 15 | 6.6 | 2256 | 1146 | 0.23 | 0.0046896 |  | 1.373 |  | 1040 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05006016 | 19.5 | 23.5 | 16 | 6.6 | 2397 | 1218 | 0.24 | 0.014756 |  | 1.464 |  | 1139 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05006020 | 19.5 | 23.5 | 20 | 8.6 | 3156 | 1603 | 0.32 | 0.007115 |  | 1.373 |  | 1455 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05006021 | 19.5 | 23.5 | 21 | 8.6 | 3238 | 1645 | 0.32 | 0.010102 |  | 1.485 |  | 1549 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05007006 | 19.5 | 27.5 | 06 | 3.3 | 1438 | 626 | 0.14 | 0.0065644 |  | 1.372 |  | 663 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05007010 | 19.5 | 27.5 | 10 | 4.6 | 1627 | 708 | 0.16 | 0.0023206 |  | 1.385 |  | 753 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05007011 | 19.5 | 27.5 | 11 | 4.6 | 2059 | 897 | 0.21 | 0.0066259 |  | 1.438 |  | 970 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05007015 | 19.5 | 27.5 | 15 | 6.6 | 2633 | 1146 | 0.26 | 0.0061227 |  | 1.373 |  | 1214 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05007016 | 19.5 | 27.5 | 16 | 6.6 | 2797 | 1218 | 0.28 | 0.020365 |  | 1.464 |  | 1329 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05007020 | 19.5 | 27.5 | 20 | 8.6 | 3683 | 1604 | 0.37 | 0.0096517 |  | 1.373 |  | 1698 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05007021 | 19.5 | 27.5 | 21 | 8.6 | 3777 | 1645 | 0.38 | 0.014525 |  | 1.485 |  | 1807 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05008006 | 19.5 | 31.5 | 06 | 3.3 | 1645 | 627 | 0.16 | 0.0090947 |  | 1.372 |  | 758 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05008010 | 19.5 | 31.5 | 10 | 4.6 | 1860 | 709 | 0.19 | 0.0034042 |  | 1.385 |  | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05008011 | 19.5 | 31.5 | 11 | 4.6 | 2354 | 897 | 0.24 | 0.0090809 |  | 1.438 |  | 1109 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05008015 | 19.5 | 31.5 | 15 | 6.6 | 3008 | 1146 | 0.3 | 0.0083046 |  | 1.373 |  | 1387 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05008016 | 19.5 | 31.5 | 16 | 6.6 | 3195 | 1217 | 0.32 | 0.026948 |  | 1.464 |  | 1518 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05008020 | 19.5 | 31.5 | 20 | 8.6 | 4208 | 1603 | 0.42 | 0.012608 |  | 1.373 |  | 1940 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05008021 | 19.5 | 31.5 | 21 | 8.6 | 4318 | 1645 | 0.43 | 0.018957 |  | 1.485 |  | 2066 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05009006 | 19.5 | 35.5 | 06 | 3.3 | 1848 | 626 | 0.18 | 0.012184 |  | 1.372 |  | 852 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05009010 | 19.5 | 35.5 | 10 | 4.6 | 2091 | 708 | 0.21 | 0.0043329 |  | 1.385 |  | 968 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05009011 | 19.5 | 35.5 | 11 | 4.6 | 2647 | 896 | 0.26 | 0.011184 |  | 1.438 |  | 1247 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05009015 | 19.5 | 35.5 | 15 | 6.6 | 3386 | 1147 | 0.34 | 0.010855 |  | 1.373 |  | 1561 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05009016 | 19.5 | 35.5 | 16 | 6.6 | 3595 | 1218 | 0.36 | 0.03453 |  | 1.464 |  | 1708 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05009020 | 19.5 | 35.5 | 20 | 8.6 | 4735 | 1604 | 0.47 | 0.015994 |  | 1.373 |  | 2183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05009021 | 19.5 | 35.5 | 21 | 8.6 | 4857 | 1645 | 0.49 | 0.025038 |  | 1.485 |  | 2324 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05010006 | 19.5 | 39.5 | 06 | 3.3 | 2055 | 626 | 0.21 | 0.017568 |  | 1.372 |  | 947 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05010010 | 19.5 | 39.5 | 10 | 4.6 | 2324 | 708 | 0.23 | 0.0053996 |  | 1.385 |  | 1076 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05010011 | 19.5 | 39.5 | 11 | 4.6 | 2942 | 897 | 0.29 | 0.014491 |  | 1.438 |  | 1386 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05010015 | 19.5 | 39.5 | 15 | 6.6 | 3761 | 1146 | 0.38 | 0.013786 |  | 1.373 |  | 1734 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05010016 | 19.5 | 39.5 | 16 | 6.6 | 3995 | 1218 | 0.4 | 0.043132 |  | 1.464 |  | 1898 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05010020 | 19.5 | 39.5 | 20 | 8.6 | 5259 | 1603 | 0.53 | 0.020575 |  | 1.373 |  | 2425 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05010021 | 19.5 | 39.5 | 21 | 8.6 | 5397 | 1645 | 0.54 | 0.030932 |  | 1.485 |  | 2582 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05011006 | 19.5 | 43.5 | 06 | 3.3 | 2261 | 627 | 0.23 | 0.022214 |  | 1.372 |  | 1042 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05011010 | 19.5 | 43.5 | 10 | 4.6 | 2558 | 709 | 0.26 | 0.0071199 |  | 1.385 |  | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05011011 | 19.5 | 43.5 | 11 | 4.6 | 3237 | 897 | 0.32 | 0.018324 |  | 1.438 |  | 1525 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05011015 | 19.5 | 43.5 | 15 | 6.6 | 4136 | 1146 | 0.41 | 0.016325 |  | 1.373 |  | 1907 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05011016 | 19.5 | 43.5 | 16 | 6.6 | 4395 | 1218 | 0.44 | 0.05278 |  | 1.464 |  | 2088 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05011020 | 19.5 | 43.5 | 20 | 8.6 | 5786 | 1603 | 0.58 | 0.024932 |  | 1.373 |  | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05011021 | 19.5 | 43.5 | 21 | 8.6 | 5936 | 1645 | 0.59 | 0.037529 |  | 1.485 |  | 2840 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05012006 | 19.5 | 47 | 06 | 3.3 | 2465 | 626 | 0.25 | 0.027613 |  | 1.372 |  | 1136 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05012010 | 19.5 | 47 | 10 | 4.6 | 2789 | 708 | 0.28 | 0.0085399 |  | 1.385 |  | 1291 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05012011 | 19.5 | 47 | 11 | 4.6 | 3530 | 897 | 0.35 | 0.022711 |  | 1.438 |  | 1663 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05012015 | 19.5 | 47 | 15 | 6.6 | 4513 | 1146 | 0.45 | 0.019964 |  | 1.373 |  | 2081 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05012016 | 19.5 | 47 | 16 | 6.6 | 4794 | 1218 | 0.48 | 0.063493 |  | 1.464 |  | 2278 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05012020 | 19.5 | 47 | 20 | 8.6 | 6311 | 1603 | 0.63 | 0.02975 |  | 1.373 |  | 2910 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05012021 | 19.5 | 47 | 21 | 8.6 | 6475 | 1645 | 0.65 | 0.04622 |  | 1.485 |  | 3098 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05014006 | 19.5 | 55 | 06 | 3.3 | 2877 | 626 | 0.29 | 0.040908 |  | 1.372 |  | 1326 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05014010 | 19.5 | 55 | 10 | 4.6 | 3253 | 708 | 0.33 | 0.012571 |  | 1.385 |  | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05014011 | 19.5 | 55 | 11 | 4.6 | 4118 | 897 | 0.41 | 0.033256 |  | 1.438 |  | 1940 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05014015 | 19.5 | 55 | 15 | 6.6 | 5266 | 1146 | 0.53 | 0.028489 |  | 1.373 |  | 2428 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05014016 | 19.5 | 55 | 16 | 6.6 | 5592 | 1217 | 0.56 | 0.088204 |  | 1.464 |  | 2657 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05014020 | 19.5 | 55 | 20 | 8.6 | 7363 | 1603 | 0.74 | 0.041905 |  | 1.373 |  | 3395 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05014021 | 19.5 | 55 | 21 | 8.6 | 7556 | 1645 | 0.76 | 0.065004 |  | 1.485 |  | 3615 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05016006 | 19.5 | 63 | 06 | 3.3 | 3287 | 626 | 0.33 | 0.05794 |  | 1.372 |  | 1515 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05016010 | 19.5 | 63 | 10 | 4.6 | 3720 | 709 | 0.37 | 0.016715 |  | 1.385 |  | 1722 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05016011 | 19.5 | 63 | 11 | 4.6 | 4708 | 897 | 0.47 | 0.046333 |  | 1.438 |  | 2218 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05016015 | 19.5 | 63 | 15 | 6.6 | 6016 | 1146 | 0.6 | 0.03753 |  | 1.373 |  | 2774 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05016016 | 19.5 | 63 | 16 | 6.6 | 6392 | 1218 | 0.64 | 0.11743 |  | 1.464 |  | 3037 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05016020 | 19.5 | 63 | 20 | 8.6 | 8415 | 1603 | 0.84 | 0.055088 |  | 1.373 |  | 3880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05016021 | 19.5 | 63 | 21 | 8.6 | 8634 | 1645 | 0.86 | 0.085528 |  | 1.485 |  | 4131 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05018006 | 19.5 | 71 | 06 | 3.3 | 3699 | 626 | 0.37 | 0.079207 |  | 1.372 |  | 1705 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05018010 | 19.5 | 71 | 10 | 4.6 | 4184 | 708 | 0.42 | 0.022597 |  | 1.385 |  | 1937 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05018011 | 19.5 | 71 | 11 | 4.6 | 5296 | 897 | 0.53 | 0.062141 |  | 1.438 |  | 2495 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05018015 | 19.5 | 71 | 15 | 6.6 | 6769 | 1146 | 0.68 | 0.049408 |  | 1.373 |  | 3121 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05018016 | 19.5 | 71 | 16 | 6.6 | 7190 | 1218 | 0.72 | 0.15133 |  | 1.464 |  | 3416 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05018020 | 19.5 | 71 | 20 | 8.6 | 9467 | 1603 | 0.95 | 0.071762 |  | 1.373 |  | 4365 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05018021 | 19.5 | 71 | 21 | 8.6 | 9715 | 1645 | 0.97 | 0.11152 |  | 1.485 |  | 4648 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05020006 | 19.5 | 78.5 | 06 | 3.3 | 4109 | 626 | 0.41 | 0.10522 |  | 1.372 |  | 1894 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05020010 | 19.5 | 78.5 | 10 | 4.6 | 4649 | 709 | 0.46 | 0.028422 |  | 1.385 |  | 2152 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05020011 | 19.5 | 78.5 | 11 | 4.6 | 5884 | 897 | 0.59 | 0.080874 |  | 1.438 |  | 2772 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05020015 | 19.5 | 78.5 | 15 | 6.6 | 7521 | 1146 | 0.75 | 0.061584 |  | 1.373 |  | 3468 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05020016 | 19.5 | 78.5 | 16 | 6.6 | 7989 | 1218 | 0.8 | 0.19007 |  | 1.464 |  | 3796 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05020020 | 19.5 | 78.5 | 20 | 8.6 | 10519 | 1603 | 1.05 | 0.089252 |  | 1.373 |  | 4850 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05020021 | 19.5 | 78.5 | 21 | 8.6 | 10793 | 1645 | 1.08 | 0.14151 |  | 1.485 |  | 5164 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05024006 | 19.5 | 94.5 | 06 | 3.3 | 4931 | 626 | 0.49 | 0.17353 |  | 1.372 |  | 2273 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05024010 | 19.5 | 94.5 | 10 | 4.6 | 5578 | 708 | 0.56 | 0.045609 |  | 1.385 |  | 2582 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05024011 | 19.5 | 94.5 | 11 | 4.6 | 7060 | 897 | 0.71 | 0.12785 |  | 1.438 |  | 3326 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05024015 | 19.5 | 94.5 | 15 | 6.6 | 9027 | 1146 | 0.9 | 0.092669 |  | 1.373 |  | 4162 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05024016 | 19.5 | 94.5 | 16 | 6.6 | 9587 | 1218 | 0.96 | 0.28261 |  | 1.464 |  | 4555 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05024020 | 19.5 | 94.5 | 20 | 8.6 | 12623 | 1603 | 1.26 | 0.13282 |  | 1.373 |  | 5820 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05024021 | 19.5 | 94.5 | 21 | 8.6 | 12952 | 1645 | 1.3 | 0.21406 |  | 1.485 |  | 6197 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.05028006 | 19.5 | 110 | 06 | 3.3 | 5754 | 626 | 0.58 | 0.27705 |  | 1.372 |  | 2652 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.05028010 | 19.5 | 110 | 10 | 4.6 | 6509 | 709 | 0.65 | 0.066091 |  | 1.385 |  | 3013 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.05028011 | 19.5 | 110 | 11 | 4.6 | 8239 | 897 | 0.82 | 0.18457 |  | 1.438 |  | 3881 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.05028015 | 19.5 | 110 | 15 | 6.6 | 10530 | 1146 | 1.05 | 0.1313 |  | 1.373 |  | 4855 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.05028016 | 19.5 | 110 | 16 | 6.6 | 11184 | 1217 | 1.12 | 0.39621 |  | 1.464 |  | 5314 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.05028020 | 19.5 | 110 | 20 | 8.6 | 14726 | 1603 | 1.47 | 0.18636 |  | 1.373 |  | 6790 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.05028021 | 19.5 | 110 | 21 | 8.6 | 15112 | 1645 | 1.51 | 0.30058 |  | 1.485 |  | 7230 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06505006 | 25.5 | 19.5 | 06 | 3.3 | 1165 | 710 | 0.12 | 0.0042833 |  | 1.35 |  | 533 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06505010 | 25.5 | 19.5 | 10 | 4.6 | 1315 | 802 | 0.13 | 0.0013751 |  | 1.371 |  | 606 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06505011 | 25.5 | 19.5 | 11 | 4.6 | 1639 | 999 | 0.16 | 0.0034202 |  | 1.437 |  | 772 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06505015 | 25.5 | 19.5 | 15 | 6.6 | 2097 | 1278 | 0.21 | 0.0038149 |  | 1.355 |  | 961 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06505016 | 25.5 | 19.5 | 16 | 6.6 | 2283 | 1392 | 0.23 | 0.013316 |  | 1.47 |  | 1087 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06505020 | 25.5 | 19.5 | 20 | 8.6 | 2930 | 1786 | 0.29 | 0.0057444 |  | 1.355 |  | 1343 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06505021 | 25.5 | 19.5 | 21 | 8.6 | 3154 | 1923 | 0.32 | 0.0098341 |  | 1.497 |  | 1515 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06506006 | 25.5 | 23.5 | 06 | 3.3 | 1399 | 711 | 0.14 | 0.0062112 |  | 1.35 |  | 640 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06506010 | 25.5 | 23.5 | 10 | 4.6 | 1578 | 802 | 0.16 | 0.0021885 |  | 1.371 |  | 727 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06506011 | 25.5 | 23.5 | 11 | 4.6 | 1966 | 999 | 0.2 | 0.0056486 |  | 1.437 |  | 926 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06506015 | 25.5 | 23.5 | 15 | 6.6 | 2516 | 1278 | 0.25 | 0.0055254 |  | 1.355 |  | 1153 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06506016 | 25.5 | 23.5 | 16 | 6.6 | 2739 | 1391 | 0.27 | 0.018626 |  | 1.47 |  | 1304 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06506020 | 25.5 | 23.5 | 20 | 8.6 | 3515 | 1786 | 0.35 | 0.0084937 |  | 1.355 |  | 1611 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06506021 | 25.5 | 23.5 | 21 | 8.6 | 3785 | 1923 | 0.38 | 0.014165 |  | 1.497 |  | 1818 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06507006 | 25.5 | 27.5 | 06 | 3.3 | 1630 | 710 | 0.16 | 0.0086243 |  | 1.35 |  | 746 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06507010 | 25.5 | 27.5 | 10 | 4.6 | 1840 | 801 | 0.18 | 0.0029084 |  | 1.371 |  | 848 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06507011 | 25.5 | 27.5 | 11 | 4.6 | 2293 | 998 | 0.23 | 0.0078807 |  | 1.437 |  | 1080 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06507015 | 25.5 | 27.5 | 15 | 6.6 | 2934 | 1278 | 0.29 | 0.0075855 |  | 1.355 |  | 1345 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06507016 | 25.5 | 27.5 | 16 | 6.6 | 3195 | 1391 | 0.32 | 0.026508 |  | 1.47 |  | 1521 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06507020 | 25.5 | 27.5 | 20 | 8.6 | 4102 | 1786 | 0.41 | 0.011818 |  | 1.355 |  | 1880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06507021 | 25.5 | 27.5 | 21 | 8.6 | 4416 | 1923 | 0.44 | 0.019366 |  | 1.497 |  | 2121 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06508006 | 25.5 | 31.5 | 06 | 3.3 | 1864 | 710 | 0.19 | 0.012935 |  | 1.35 |  | 853 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06508010 | 25.5 | 31.5 | 10 | 4.6 | 2103 | 801 | 0.21 | 0.0041212 |  | 1.371 |  | 969 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06508011 | 25.5 | 31.5 | 11 | 4.6 | 2620 | 998 | 0.26 | 0.010571 |  | 1.437 |  | 1234 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06508015 | 25.5 | 31.5 | 15 | 6.6 | 3356 | 1279 | 0.34 | 0.01061 |  | 1.355 |  | 1538 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06508016 | 25.5 | 31.5 | 16 | 6.6 | 3651 | 1391 | 0.37 | 0.035876 |  | 1.47 |  | 1738 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06508020 | 25.5 | 31.5 | 20 | 8.6 | 4686 | 1785 | 0.47 | 0.015734 |  | 1.355 |  | 2148 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06508021 | 25.5 | 31.5 | 21 | 8.6 | 5046 | 1923 | 0.5 | 0.025469 |  | 1.497 |  | 2424 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06509006 | 25.5 | 35.5 | 06 | 3.3 | 2096 | 710 | 0.21 | 0.016725 |  | 1.35 |  | 959 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06509010 | 25.5 | 35.5 | 10 | 4.6 | 2366 | 801 | 0.24 | 0.0055865 |  | 1.371 |  | 1090 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06509011 | 25.5 | 35.5 | 11 | 4.6 | 2950 | 999 | 0.3 | 0.01466 |  | 1.437 |  | 1389 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06509015 | 25.5 | 35.5 | 15 | 6.6 | 3774 | 1278 | 0.38 | 0.01349 |  | 1.355 |  | 1730 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06509016 | 25.5 | 35.5 | 16 | 6.6 | 4109 | 1392 | 0.41 | 0.044601 |  | 1.47 |  | 1956 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06509020 | 25.5 | 35.5 | 20 | 8.6 | 5273 | 1786 | 0.53 | 0.020256 |  | 1.355 |  | 2417 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06509021 | 25.5 | 35.5 | 21 | 8.6 | 5677 | 1923 | 0.57 | 0.033647 |  | 1.497 |  | 2727 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06510006 | 25.5 | 39.5 | 06 | 3.3 | 2330 | 710 | 0.23 | 0.02119 |  | 1.35 |  | 1066 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06510010 | 25.5 | 39.5 | 10 | 4.6 | 2628 | 801 | 0.26 | 0.0068133 |  | 1.371 |  | 1211 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06510011 | 25.5 | 39.5 | 11 | 4.6 | 3277 | 999 | 0.33 | 0.018487 |  | 1.437 |  | 1543 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06510015 | 25.5 | 39.5 | 15 | 6.6 | 4193 | 1278 | 0.42 | 0.016757 |  | 1.355 |  | 1922 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06510016 | 25.5 | 39.5 | 16 | 6.6 | 4564 | 1391 | 0.46 | 0.056765 |  | 1.47 |  | 2173 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06510020 | 25.5 | 39.5 | 20 | 8.6 | 5858 | 1786 | 0.59 | 0.025397 |  | 1.355 |  | 2685 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06510021 | 25.5 | 39.5 | 21 | 8.6 | 6308 | 1923 | 0.63 | 0.041779 |  | 1.497 |  | 3030 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06511006 | 25.5 | 43.5 | 06 | 3.3 | 2563 | 710 | 0.26 | 0.028613 |  | 1.35 |  | 1173 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06511010 | 25.5 | 43.5 | 10 | 4.6 | 2891 | 801 | 0.29 | 0.0087536 |  | 1.371 |  | 1332 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06511011 | 25.5 | 43.5 | 11 | 4.6 | 3604 | 999 | 0.36 | 0.022864 |  | 1.437 |  | 1697 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06511015 | 25.5 | 43.5 | 15 | 6.6 | 4612 | 1278 | 0.46 | 0.020423 |  | 1.355 |  | 2114 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06511016 | 25.5 | 43.5 | 16 | 6.6 | 5020 | 1391 | 0.5 | 0.067829 |  | 1.47 |  | 2390 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06511020 | 25.5 | 43.5 | 20 | 8.6 | 6445 | 1786 | 0.64 | 0.03024 |  | 1.355 |  | 2954 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06511021 | 25.5 | 43.5 | 21 | 8.6 | 6939 | 1923 | 0.69 | 0.050901 |  | 1.497 |  | 3333 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06512006 | 25.5 | 47 | 06 | 3.3 | 2795 | 710 | 0.28 | 0.034908 |  | 1.35 |  | 1279 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06512010 | 25.5 | 47 | 10 | 4.6 | 3153 | 801 | 0.32 | 0.010987 |  | 1.371 |  | 1453 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06512011 | 25.5 | 47 | 11 | 4.6 | 3933 | 999 | 0.39 | 0.027818 |  | 1.437 |  | 1852 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06512015 | 25.5 | 47 | 15 | 6.6 | 5031 | 1278 | 0.5 | 0.024499 |  | 1.355 |  | 2306 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06512016 | 25.5 | 47 | 16 | 6.6 | 5478 | 1391 | 0.55 | 0.082909 |  | 1.47 |  | 2608 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06512020 | 25.5 | 47 | 20 | 8.6 | 7030 | 1786 | 0.7 | 0.036566 |  | 1.355 |  | 3222 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06512021 | 25.5 | 47 | 21 | 8.6 | 7570 | 1923 | 0.76 | 0.06263 |  | 1.497 |  | 3636 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06514006 | 25.5 | 55 | 06 | 3.3 | 3261 | 710 | 0.33 | 0.053492 |  | 1.35 |  | 1492 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06514010 | 25.5 | 55 | 10 | 4.6 | 3679 | 801 | 0.37 | 0.015585 |  | 1.371 |  | 1695 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06514011 | 25.5 | 55 | 11 | 4.6 | 4587 | 999 | 0.46 | 0.041219 |  | 1.437 |  | 2160 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06514015 | 25.5 | 55 | 15 | 6.6 | 5871 | 1278 | 0.59 | 0.035066 |  | 1.355 |  | 2691 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06514016 | 25.5 | 55 | 16 | 6.6 | 6390 | 1391 | 0.64 | 0.11452 |  | 1.47 |  | 3042 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06514020 | 25.5 | 55 | 20 | 8.6 | 8201 | 1785 | 0.82 | 0.051209 |  | 1.355 |  | 3759 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06514021 | 25.5 | 55 | 21 | 8.6 | 8831 | 1923 | 0.88 | 0.086354 |  | 1.497 |  | 4242 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06516006 | 25.5 | 63 | 06 | 3.3 | 3728 | 710 | 0.37 | 0.073522 |  | 1.35 |  | 1706 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06516010 | 25.5 | 63 | 10 | 4.6 | 4206 | 801 | 0.42 | 0.021188 |  | 1.371 |  | 1938 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06516011 | 25.5 | 63 | 11 | 4.6 | 5243 | 999 | 0.52 | 0.055907 |  | 1.437 |  | 2469 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06516015 | 25.5 | 63 | 15 | 6.6 | 6709 | 1278 | 0.67 | 0.046443 |  | 1.355 |  | 3075 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06516016 | 25.5 | 63 | 16 | 6.6 | 7303 | 1391 | 0.73 | 0.1518 |  | 1.47 |  | 3477 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06516020 | 25.5 | 63 | 20 | 8.6 | 9373 | 1786 | 0.94 | 0.068589 |  | 1.355 |  | 4296 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06516021 | 25.5 | 63 | 21 | 8.6 | 10093 | 1923 | 1.01 | 0.11668 |  | 1.497 |  | 4848 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06518006 | 25.5 | 71 | 06 | 3.3 | 4194 | 710 | 0.42 | 0.10319 |  | 1.35 |  | 1919 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06518010 | 25.5 | 71 | 10 | 4.6 | 4731 | 801 | 0.47 | 0.027867 |  | 1.371 |  | 2180 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06518011 | 25.5 | 71 | 11 | 4.6 | 5897 | 999 | 0.59 | 0.075792 |  | 1.437 |  | 2777 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06518015 | 25.5 | 71 | 15 | 6.6 | 7549 | 1278 | 0.75 | 0.059669 |  | 1.355 |  | 3460 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06518016 | 25.5 | 71 | 16 | 6.6 | 8215 | 1391 | 0.82 | 0.19494 |  | 1.47 |  | 3911 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06518020 | 25.5 | 71 | 20 | 8.6 | 10544 | 1785 | 1.05 | 0.087181 |  | 1.355 |  | 4833 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06518021 | 25.5 | 71 | 21 | 8.6 | 11354 | 1923 | 1.14 | 0.15223 |  | 1.497 |  | 5454 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06520006 | 25.5 | 78.5 | 06 | 3.3 | 4659 | 710 | 0.47 | 0.14 |  | 1.35 |  | 2132 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06520010 | 25.5 | 78.5 | 10 | 4.6 | 5256 | 801 | 0.53 | 0.03698 |  | 1.371 |  | 2422 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06520011 | 25.5 | 78.5 | 11 | 4.6 | 6553 | 999 | 0.66 | 0.099473 |  | 1.437 |  | 3086 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06520015 | 25.5 | 78.5 | 15 | 6.6 | 8387 | 1278 | 0.84 | 0.076565 |  | 1.355 |  | 3844 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06520016 | 25.5 | 78.5 | 16 | 6.6 | 9129 | 1391 | 0.91 | 0.24413 |  | 1.47 |  | 4346 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06520020 | 25.5 | 78.5 | 20 | 8.6 | 11716 | 1786 | 1.17 | 0.11011 |  | 1.355 |  | 5370 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06520021 | 25.5 | 78.5 | 21 | 8.6 | 12616 | 1923 | 1.26 | 0.1903 |  | 1.497 |  | 6060 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06524006 | 25.5 | 94.5 | 06 | 3.3 | 5590 | 710 | 0.56 | 0.22966 |  | 1.35 |  | 2558 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06524010 | 25.5 | 94.5 | 10 | 4.6 | 6307 | 801 | 0.63 | 0.056705 |  | 1.371 |  | 2906 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06524011 | 25.5 | 94.5 | 11 | 4.6 | 7863 | 999 | 0.79 | 0.15556 |  | 1.437 |  | 3703 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06524015 | 25.5 | 94.5 | 15 | 6.6 | 10064 | 1278 | 1.01 | 0.11554 |  | 1.355 |  | 4613 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06524016 | 25.5 | 94.5 | 16 | 6.6 | 10954 | 1391 | 1.1 | 0.36785 |  | 1.47 |  | 5215 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06524020 | 25.5 | 94.5 | 20 | 8.6 | 14059 | 1785 | 1.41 | 0.1651 |  | 1.355 |  | 6444 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06524021 | 25.5 | 94.5 | 21 | 8.6 | 15139 | 1923 | 1.51 | 0.28509 |  | 1.497 |  | 7272 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.06528006 | 25.5 | 110 | 06 | 3.3 | 6523 | 710 | 0.65 | 0.35213 |  | 1.35 |  | 2985 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.06528010 | 25.5 | 110 | 10 | 4.6 | 7359 | 801 | 0.74 | 0.08391 |  | 1.371 |  | 3391 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.06528011 | 25.5 | 110 | 11 | 4.6 | 9174 | 999 | 0.92 | 0.22782 |  | 1.437 |  | 4320 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.06528015 | 25.5 | 110 | 15 | 6.6 | 11742 | 1278 | 1.17 | 0.16136 |  | 1.355 |  | 5382 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.06528016 | 25.5 | 110 | 16 | 6.6 | 12779 | 1391 | 1.28 | 0.51269 |  | 1.47 |  | 6084 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.06528020 | 25.5 | 110 | 20 | 8.6 | 16402 | 1785 | 1.64 | 0.23012 |  | 1.355 |  | 7518 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.06528021 | 25.5 | 110 | 21 | 8.6 | 17662 | 1923 | 1.77 | 0.40689 |  | 1.497 |  | 8484 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09506006 | 37.5 | 23.5 | 06 | 3.3 | 1631 | 829 | 0.16 | 0.008154 |  | 1.307 |  | 736 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09506010 | 37.5 | 23.5 | 10 | 4.6 | 1831 | 930 | 0.18 | 0.0027464 |  | 1.343 |  | 836 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09506011 | 37.5 | 23.5 | 11 | 4.6 | 2291 | 1164 | 0.23 | 0.0073849 |  | 1.434 |  | 1078 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09506015 | 37.5 | 23.5 | 15 | 6.6 | 2843 | 1444 | 0.28 | 0.0069056 |  | 1.32 |  | 1288 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09506016 | 37.5 | 23.5 | 16 | 6.6 | 3360 | 1707 | 0.34 | 0.029389 |  | 1.482 |  | 1606 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09506020 | 37.5 | 23.5 | 20 | 8.6 | 3962 | 2013 | 0.4 | 0.01106 |  | 1.32 |  | 1795 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09506021 | 37.5 | 23.5 | 21 | 8.6 | 4856 | 2467 | 0.49 | 0.023366 |  | 1.522 |  | 2352 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09507006 | 37.5 | 27.5 | 06 | 3.3 | 1902 | 828 | 0.19 | 0.012255 |  | 1.307 |  | 858 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09507010 | 37.5 | 27.5 | 10 | 4.6 | 2136 | 930 | 0.21 | 0.0039095 |  | 1.343 |  | 975 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09507011 | 37.5 | 27.5 | 11 | 4.6 | 2672 | 1163 | 0.27 | 0.010702 |  | 1.434 |  | 1257 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09507015 | 37.5 | 27.5 | 15 | 6.6 | 3315 | 1443 | 0.33 | 0.0097754 |  | 1.32 |  | 1502 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09507016 | 37.5 | 27.5 | 16 | 6.6 | 3921 | 1707 | 0.39 | 0.03918 |  | 1.482 |  | 1874 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09507020 | 37.5 | 27.5 | 20 | 8.6 | 4622 | 2013 | 0.46 | 0.014831 |  | 1.32 |  | 2094 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09507021 | 37.5 | 27.5 | 21 | 8.6 | 5666 | 2467 | 0.57 | 0.0322 |  | 1.522 |  | 2744 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09508006 | 37.5 | 31.5 | 06 | 3.3 | 2174 | 828 | 0.22 | 0.017472 |  | 1.307 |  | 981 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09508010 | 37.5 | 31.5 | 10 | 4.6 | 2440 | 930 | 0.24 | 0.0053196 |  | 1.343 |  | 1114 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09508011 | 37.5 | 31.5 | 11 | 4.6 | 3054 | 1164 | 0.31 | 0.014767 |  | 1.434 |  | 1437 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09508015 | 37.5 | 31.5 | 15 | 6.6 | 3790 | 1444 | 0.38 | 0.013193 |  | 1.32 |  | 1717 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09508016 | 37.5 | 31.5 | 16 | 6.6 | 4481 | 1707 | 0.45 | 0.052778 |  | 1.482 |  | 2142 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09508020 | 37.5 | 31.5 | 20 | 8.6 | 5284 | 2013 | 0.53 | 0.019937 |  | 1.32 |  | 2394 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09508021 | 37.5 | 31.5 | 21 | 8.6 | 6475 | 2467 | 0.65 | 0.042592 |  | 1.522 |  | 3136 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09509006 | 37.5 | 35.5 | 06 | 3.3 | 2445 | 828 | 0.24 | 0.022009 |  | 1.307 |  | 1103 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09509010 | 37.5 | 35.5 | 10 | 4.6 | 2747 | 930 | 0.27 | 0.0069919 |  | 1.343 |  | 1254 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09509011 | 37.5 | 35.5 | 11 | 4.6 | 3435 | 1163 | 0.34 | 0.018581 |  | 1.434 |  | 1616 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09509015 | 37.5 | 35.5 | 15 | 6.6 | 4262 | 1443 | 0.43 | 0.017177 |  | 1.32 |  | 1931 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09509016 | 37.5 | 35.5 | 16 | 6.6 | 5040 | 1707 | 0.5 | 0.065925 |  | 1.482 |  | 2409 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09509020 | 37.5 | 35.5 | 20 | 8.6 | 5944 | 2013 | 0.59 | 0.025014 |  | 1.32 |  | 2693 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09509021 | 37.5 | 35.5 | 21 | 8.6 | 7284 | 2467 | 0.73 | 0.054591 |  | 1.522 |  | 3528 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09510006 | 37.5 | 39.5 | 06 | 3.3 | 2718 | 828 | 0.27 | 0.029487 |  | 1.307 |  | 1226 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09510010 | 37.5 | 39.5 | 10 | 4.6 | 3051 | 930 | 0.31 | 0.0095155 |  | 1.343 |  | 1393 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09510011 | 37.5 | 39.5 | 11 | 4.6 | 3818 | 1164 | 0.38 | 0.024126 |  | 1.434 |  | 1796 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09510015 | 37.5 | 39.5 | 15 | 6.6 | 4736 | 1444 | 0.47 | 0.020868 |  | 1.32 |  | 2146 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09510016 | 37.5 | 39.5 | 16 | 6.6 | 5601 | 1707 | 0.56 | 0.083576 |  | 1.482 |  | 2677 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09510020 | 37.5 | 39.5 | 20 | 8.6 | 6604 | 2013 | 0.66 | 0.031655 |  | 1.32 |  | 2992 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09510021 | 37.5 | 39.5 | 21 | 8.6 | 8094 | 2467 | 0.81 | 0.068243 |  | 1.522 |  | 3920 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09511006 | 37.5 | 43.5 | 06 | 3.3 | 2990 | 829 | 0.3 | 0.038453 |  | 1.307 |  | 1349 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09511010 | 37.5 | 43.5 | 10 | 4.6 | 3356 | 930 | 0.34 | 0.011831 |  | 1.343 |  | 1532 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09511011 | 37.5 | 43.5 | 11 | 4.6 | 4200 | 1164 | 0.42 | 0.030557 |  | 1.434 |  | 1976 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09511015 | 37.5 | 43.5 | 15 | 6.6 | 5211 | 1444 | 0.52 | 0.02593 |  | 1.32 |  | 2361 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09511016 | 37.5 | 43.5 | 16 | 6.6 | 6162 | 1707 | 0.62 | 0.10349 |  | 1.482 |  | 2945 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09511020 | 37.5 | 43.5 | 20 | 8.6 | 7264 | 2013 | 0.73 | 0.039145 |  | 1.32 |  | 3291 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09511021 | 37.5 | 43.5 | 21 | 8.6 | 8903 | 2467 | 0.89 | 0.083592 |  | 1.522 |  | 4312 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09512006 | 37.5 | 47 | 06 | 3.3 | 3261 | 828 | 0.33 | 0.049045 |  | 1.307 |  | 1471 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09512010 | 37.5 | 47 | 10 | 4.6 | 3662 | 930 | 0.37 | 0.014454 |  | 1.343 |  | 1672 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09512011 | 37.5 | 47 | 11 | 4.6 | 4581 | 1164 | 0.46 | 0.037919 |  | 1.434 |  | 2155 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09512015 | 37.5 | 47 | 15 | 6.6 | 5683 | 1443 | 0.57 | 0.031607 |  | 1.32 |  | 2575 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09512016 | 37.5 | 47 | 16 | 6.6 | 6720 | 1707 | 0.67 | 0.1221 |  | 1.482 |  | 3212 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09512020 | 37.5 | 47 | 20 | 8.6 | 7923 | 2012 | 0.79 | 0.046344 |  | 1.32 |  | 3590 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09512021 | 37.5 | 47 | 21 | 8.6 | 9713 | 2467 | 0.97 | 0.10068 |  | 1.522 |  | 4704 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Strada | STRW.09514006 | 37.5 | 55 | 06 | 3.3 | 3804 | 828 | 0.38 | 0.0717 |  | 1.307 |  | 1716 | [19 empty] | 0.00016126 | 2.1459 | 4 | 0.0013916
Horizontal Wall | Strada | STRW.09514010 | 37.5 | 55 | 10 | 4.6 | 4271 | 930 | 0.43 | 0.020674 |  | 1.343 |  | 1950 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada | STRW.09514011 | 37.5 | 55 | 11 | 4.6 | 5344 | 1163 | 0.53 | 0.053703 |  | 1.434 |  | 2514 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Strada | STRW.09514015 | 37.5 | 55 | 15 | 6.6 | 6630 | 1443 | 0.66 | 0.043577 |  | 1.32 |  | 3004 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada | STRW.09514016 | 37.5 | 55 | 16 | 6.6 | 7842 | 1707 | 0.78 | 0.16866 |  | 1.482 |  | 3748 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Strada | STRW.09514020 | 37.5 | 55 | 20 | 8.6 | 9246 | 2013 | 0.92 | 0.064124 |  | 1.32 |  | 4189 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada | STRW.09514021 | 37.5 | 55 | 21 | 8.6 | 11331 | 2467 | 1.13 | 0.14026 |  | 1.522 |  | 5488 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.02004010 | 8 | 15.5 | 10 | 4.6 | 561 | 427 | 0.06 | 0.00028475 |  | 1.413 |  | 262 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02004015 | 8 | 15.5 | 15 | 6.6 | 935 | 712 | 0.09 | 0.00069432 |  | 1.408 |  | 436 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02004020 | 8 | 15.5 | 20 | 8.6 | 1314 | 1001 | 0.13 | 0.0011462 |  | 1.408 |  | 613 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02005010 | 8 | 19.5 | 10 | 4.6 | 702 | 428 | 0.07 | 0.00041569 |  | 1.413 |  | 328 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02005015 | 8 | 19.5 | 15 | 6.6 | 1168 | 712 | 0.12 | 0.0012664 |  | 1.408 |  | 545 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02005020 | 8 | 19.5 | 20 | 8.6 | 1642 | 1001 | 0.16 | 0.0017706 |  | 1.408 |  | 766 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02006010 | 8 | 23.5 | 10 | 4.6 | 841 | 427 | 0.08 | 0.00057754 |  | 1.413 |  | 393 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02006015 | 8 | 23.5 | 15 | 6.6 | 1402 | 712 | 0.14 | 0.0017685 |  | 1.408 |  | 654 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02006020 | 8 | 23.5 | 20 | 8.6 | 1970 | 1001 | 0.2 | 0.0028126 |  | 1.408 |  | 919 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02007010 | 8 | 27.5 | 10 | 4.6 | 982 | 428 | 0.1 | 0.0009446 |  | 1.413 |  | 459 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02007015 | 8 | 27.5 | 15 | 6.6 | 1636 | 712 | 0.16 | 0.0023652 |  | 1.408 |  | 763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02007020 | 8 | 27.5 | 20 | 8.6 | 2298 | 1001 | 0.23 | 0.0037818 |  | 1.408 |  | 1072 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02008010 | 8 | 31.5 | 10 | 4.6 | 1122 | 427 | 0.11 | 0.0012021 |  | 1.413 |  | 524 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02008015 | 8 | 31.5 | 15 | 6.6 | 1869 | 712 | 0.19 | 0.0034008 |  | 1.408 |  | 872 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02008020 | 8 | 31.5 | 20 | 8.6 | 2628 | 1001 | 0.26 | 0.0049082 |  | 1.408 |  | 1226 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02009010 | 8 | 35.5 | 10 | 4.6 | 1263 | 428 | 0.13 | 0.0017437 |  | 1.413 |  | 590 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02009015 | 8 | 35.5 | 15 | 6.6 | 2103 | 712 | 0.21 | 0.0042415 |  | 1.408 |  | 981 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02009020 | 8 | 35.5 | 20 | 8.6 | 2956 | 1001 | 0.3 | 0.0066224 |  | 1.408 |  | 1379 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02010010 | 8 | 39.5 | 10 | 4.6 | 1402 | 427 | 0.14 | 0.0021113 |  | 1.413 |  | 655 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02010015 | 8 | 39.5 | 15 | 6.6 | 2337 | 712 | 0.23 | 0.0051886 |  | 1.408 |  | 1090 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02010020 | 8 | 39.5 | 20 | 8.6 | 3284 | 1001 | 0.33 | 0.0081256 |  | 1.408 |  | 1532 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02011010 | 8 | 43.5 | 10 | 4.6 | 1543 | 428 | 0.15 | 0.0025231 |  | 1.413 |  | 721 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02011015 | 8 | 43.5 | 15 | 6.6 | 2571 | 712 | 0.26 | 0.0067392 |  | 1.408 |  | 1199 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02011020 | 8 | 43.5 | 20 | 8.6 | 3613 | 1001 | 0.36 | 0.0097997 |  | 1.408 |  | 1685 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02012010 | 8 | 47 | 10 | 4.6 | 1682 | 427 | 0.17 | 0.0033402 |  | 1.413 |  | 786 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02012015 | 8 | 47 | 15 | 6.6 | 2804 | 712 | 0.28 | 0.0079564 |  | 1.408 |  | 1308 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02012020 | 8 | 47 | 20 | 8.6 | 3941 | 1001 | 0.39 | 0.011649 |  | 1.408 |  | 1838 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02014010 | 8 | 55 | 10 | 4.6 | 1963 | 427 | 0.2 | 0.0049216 |  | 1.413 |  | 917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02014015 | 8 | 55 | 15 | 6.6 | 3272 | 712 | 0.33 | 0.011403 |  | 1.408 |  | 1526 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02014020 | 8 | 55 | 20 | 8.6 | 4599 | 1001 | 0.46 | 0.016582 |  | 1.408 |  | 2145 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02016010 | 8 | 63 | 10 | 4.6 | 2243 | 427 | 0.22 | 0.0063403 |  | 1.413 |  | 1048 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02016015 | 8 | 63 | 15 | 6.6 | 3739 | 712 | 0.37 | 0.014787 |  | 1.408 |  | 1744 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02016020 | 8 | 63 | 20 | 8.6 | 5255 | 1001 | 0.53 | 0.022489 |  | 1.408 |  | 2451 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02018010 | 8 | 71 | 10 | 4.6 | 2524 | 427 | 0.25 | 0.0086163 |  | 1.413 |  | 1179 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02018015 | 8 | 71 | 15 | 6.6 | 4206 | 712 | 0.42 | 0.019575 |  | 1.408 |  | 1962 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02018020 | 8 | 71 | 20 | 8.6 | 5913 | 1001 | 0.59 | 0.028468 |  | 1.408 |  | 2758 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02020010 | 8 | 78.5 | 10 | 4.6 | 2804 | 427 | 0.28 | 0.011329 |  | 1.413 |  | 1310 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02020015 | 8 | 78.5 | 15 | 6.6 | 4674 | 712 | 0.47 | 0.025145 |  | 1.408 |  | 2180 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02020020 | 8 | 78.5 | 20 | 8.6 | 6569 | 1001 | 0.66 | 0.03631 |  | 1.408 |  | 3064 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02022010 | 8 | 86.5 | 10 | 4.6 | 3084 | 427 | 0.31 | 0.014508 |  | 1.413 |  | 1441 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02022015 | 8 | 86.5 | 15 | 6.6 | 5141 | 712 | 0.51 | 0.030384 |  | 1.408 |  | 2398 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02022020 | 8 | 86.5 | 20 | 8.6 | 7225 | 1001 | 0.72 | 0.044048 |  | 1.408 |  | 3370 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02024010 | 8 | 94.5 | 10 | 4.6 | 3365 | 427 | 0.34 | 0.018179 |  | 1.413 |  | 1572 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02024015 | 8 | 94.5 | 15 | 6.6 | 5608 | 712 | 0.56 | 0.03748 |  | 1.408 |  | 2616 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02024020 | 8 | 94.5 | 20 | 8.6 | 7883 | 1001 | 0.79 | 0.053957 |  | 1.408 |  | 3677 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02026010 | 8 | 102.5 | 10 | 4.6 | 3645 | 427 | 0.36 | 0.021273 |  | 1.413 |  | 1703 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02026015 | 8 | 102.5 | 15 | 6.6 | 6076 | 712 | 0.61 | 0.045451 |  | 1.408 |  | 2834 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02026020 | 8 | 102.5 | 20 | 8.6 | 8539 | 1001 | 0.85 | 0.06357 |  | 1.408 |  | 3983 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02028010 | 8 | 110 | 10 | 4.6 | 3925 | 427 | 0.39 | 0.025879 |  | 1.413 |  | 1834 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02028015 | 8 | 110 | 15 | 6.6 | 6543 | 712 | 0.65 | 0.052778 |  | 1.408 |  | 3052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02028020 | 8 | 110 | 20 | 8.6 | 9197 | 1001 | 0.92 | 0.07567 |  | 1.408 |  | 4290 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.02030010 | 8 | 118 | 10 | 4.6 | 4206 | 427 | 0.42 | 0.031051 |  | 1.413 |  | 1965 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.02030015 | 8 | 118 | 15 | 6.6 | 7011 | 712 | 0.7 | 0.062443 |  | 1.408 |  | 3270 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.02030020 | 8 | 118 | 20 | 8.6 | 9853 | 1001 | 0.99 | 0.088982 |  | 1.408 |  | 4596 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03004010 | 12 | 15.5 | 10 | 4.6 | 709 | 540 | 0.07 | 0.00038421 |  | 1.403 |  | 330 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03004011 | 12 | 15.5 | 11 | 4.6 | 950 | 724 | 0.1 | 0.0012679 |  | 1.44 |  | 448 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03004015 | 12 | 15.5 | 15 | 6.6 | 1171 | 892 | 0.12 | 0.0012257 |  | 1.396 |  | 544 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03004016 | 12 | 15.5 | 16 | 6.6 | 1249 | 952 | 0.12 | 0.003591 |  | 1.456 |  | 592 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03004020 | 12 | 15.5 | 20 | 8.6 | 1640 | 1250 | 0.16 | 0.0017301 |  | 1.396 |  | 762 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03004021 | 12 | 15.5 | 21 | 8.6 | 1637 | 1247 | 0.16 | 0.002428 |  | 1.468 |  | 779 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03005010 | 12 | 19.5 | 10 | 4.6 | 887 | 541 | 0.09 | 0.00067521 |  | 1.403 |  | 413 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03005011 | 12 | 19.5 | 11 | 4.6 | 1190 | 725 | 0.12 | 0.0019658 |  | 1.44 |  | 561 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03005015 | 12 | 19.5 | 15 | 6.6 | 1464 | 892 | 0.15 | 0.0019652 |  | 1.396 |  | 680 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03005016 | 12 | 19.5 | 16 | 6.6 | 1562 | 952 | 0.16 | 0.0064892 |  | 1.456 |  | 740 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03005020 | 12 | 19.5 | 20 | 8.6 | 2051 | 1250 | 0.21 | 0.0030321 |  | 1.396 |  | 953 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03005021 | 12 | 19.5 | 21 | 8.6 | 2047 | 1248 | 0.2 | 0.0038934 |  | 1.468 |  | 974 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03006010 | 12 | 23.5 | 10 | 4.6 | 1065 | 541 | 0.11 | 0.0010642 |  | 1.403 |  | 496 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03006011 | 12 | 23.5 | 11 | 4.6 | 1428 | 725 | 0.14 | 0.0028541 |  | 1.44 |  | 673 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03006015 | 12 | 23.5 | 15 | 6.6 | 1754 | 891 | 0.18 | 0.0028967 |  | 1.396 |  | 815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03006016 | 12 | 23.5 | 16 | 6.6 | 1874 | 952 | 0.19 | 0.0092992 |  | 1.456 |  | 888 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03006020 | 12 | 23.5 | 20 | 8.6 | 2462 | 1251 | 0.25 | 0.0043691 |  | 1.396 |  | 1144 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03006021 | 12 | 23.5 | 21 | 8.6 | 2457 | 1248 | 0.25 | 0.0062186 |  | 1.468 |  | 1169 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03007010 | 12 | 27.5 | 10 | 4.6 | 1241 | 540 | 0.12 | 0.0013381 |  | 1.403 |  | 578 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03007011 | 12 | 27.5 | 11 | 4.6 | 1665 | 725 | 0.17 | 0.0044311 |  | 1.44 |  | 785 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03007015 | 12 | 27.5 | 15 | 6.6 | 2047 | 891 | 0.2 | 0.003661 |  | 1.396 |  | 951 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03007016 | 12 | 27.5 | 16 | 6.6 | 2186 | 952 | 0.22 | 0.012655 |  | 1.456 |  | 1036 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03007020 | 12 | 27.5 | 20 | 8.6 | 2871 | 1250 | 0.29 | 0.0059704 |  | 1.396 |  | 1334 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03007021 | 12 | 27.5 | 21 | 8.6 | 2867 | 1248 | 0.29 | 0.0085502 |  | 1.468 |  | 1364 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03008010 | 12 | 31.5 | 10 | 4.6 | 1419 | 541 | 0.14 | 0.0019018 |  | 1.403 |  | 661 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03008011 | 12 | 31.5 | 11 | 4.6 | 1903 | 725 | 0.19 | 0.0058317 |  | 1.44 |  | 897 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03008015 | 12 | 31.5 | 15 | 6.6 | 2340 | 892 | 0.23 | 0.0049391 |  | 1.396 |  | 1087 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03008016 | 12 | 31.5 | 16 | 6.6 | 2499 | 952 | 0.25 | 0.016572 |  | 1.456 |  | 1184 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03008020 | 12 | 31.5 | 20 | 8.6 | 3282 | 1250 | 0.33 | 0.0078434 |  | 1.396 |  | 1525 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03008021 | 12 | 31.5 | 21 | 8.6 | 3275 | 1248 | 0.33 | 0.011296 |  | 1.468 |  | 1558 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03009010 | 12 | 35.5 | 10 | 4.6 | 1596 | 541 | 0.16 | 0.0025848 |  | 1.403 |  | 743 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03009011 | 12 | 35.5 | 11 | 4.6 | 2140 | 725 | 0.21 | 0.0074727 |  | 1.44 |  | 1009 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03009015 | 12 | 35.5 | 15 | 6.6 | 2632 | 891 | 0.26 | 0.0064309 |  | 1.396 |  | 1223 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03009016 | 12 | 35.5 | 16 | 6.6 | 2811 | 952 | 0.28 | 0.021066 |  | 1.456 |  | 1332 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03009020 | 12 | 35.5 | 20 | 8.6 | 3691 | 1250 | 0.37 | 0.0099954 |  | 1.396 |  | 1715 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03009021 | 12 | 35.5 | 21 | 8.6 | 3685 | 1248 | 0.37 | 0.014472 |  | 1.468 |  | 1753 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03010010 | 12 | 39.5 | 10 | 4.6 | 1774 | 541 | 0.18 | 0.0033945 |  | 1.403 |  | 826 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03010011 | 12 | 39.5 | 11 | 4.6 | 2378 | 725 | 0.24 | 0.010148 |  | 1.44 |  | 1121 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03010015 | 12 | 39.5 | 15 | 6.6 | 2925 | 892 | 0.29 | 0.0081436 |  | 1.396 |  | 1359 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03010016 | 12 | 39.5 | 16 | 6.6 | 3123 | 952 | 0.31 | 0.026149 |  | 1.456 |  | 1480 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03010020 | 12 | 39.5 | 20 | 8.6 | 4103 | 1251 | 0.41 | 0.012434 |  | 1.396 |  | 1906 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03010021 | 12 | 39.5 | 21 | 8.6 | 4094 | 1248 | 0.41 | 0.01809 |  | 1.468 |  | 1948 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03011010 | 12 | 43.5 | 10 | 4.6 | 1952 | 541 | 0.2 | 0.004338 |  | 1.403 |  | 909 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03011011 | 12 | 43.5 | 11 | 4.6 | 2616 | 725 | 0.26 | 0.012411 |  | 1.44 |  | 1233 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03011015 | 12 | 43.5 | 15 | 6.6 | 3218 | 892 | 0.32 | 0.010084 |  | 1.396 |  | 1495 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03011016 | 12 | 43.5 | 16 | 6.6 | 3435 | 952 | 0.34 | 0.031836 |  | 1.456 |  | 1628 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03011020 | 12 | 43.5 | 20 | 8.6 | 4514 | 1251 | 0.45 | 0.015165 |  | 1.396 |  | 2097 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03011021 | 12 | 43.5 | 21 | 8.6 | 4504 | 1248 | 0.45 | 0.022165 |  | 1.468 |  | 2143 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03012010 | 12 | 47 | 10 | 4.6 | 2128 | 541 | 0.21 | 0.004968 |  | 1.403 |  | 991 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03012011 | 12 | 47 | 11 | 4.6 | 2853 | 725 | 0.29 | 0.015973 |  | 1.44 |  | 1345 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03012015 | 12 | 47 | 15 | 6.6 | 3511 | 892 | 0.35 | 0.012259 |  | 1.396 |  | 1631 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03012016 | 12 | 47 | 16 | 6.6 | 3748 | 952 | 0.37 | 0.038141 |  | 1.456 |  | 1776 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03012020 | 12 | 47 | 20 | 8.6 | 4923 | 1250 | 0.49 | 0.018195 |  | 1.396 |  | 2287 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03012021 | 12 | 47 | 21 | 8.6 | 4914 | 1248 | 0.49 | 0.026711 |  | 1.468 |  | 2338 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03014010 | 12 | 55 | 10 | 4.6 | 2482 | 540 | 0.25 | 0.0074705 |  | 1.403 |  | 1156 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03014011 | 12 | 55 | 11 | 4.6 | 3328 | 725 | 0.33 | 0.022196 |  | 1.44 |  | 1569 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03014015 | 12 | 55 | 15 | 6.6 | 4096 | 892 | 0.41 | 0.017339 |  | 1.396 |  | 1903 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03014016 | 12 | 55 | 16 | 6.6 | 4372 | 952 | 0.44 | 0.05507 |  | 1.456 |  | 2072 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03014020 | 12 | 55 | 20 | 8.6 | 5743 | 1250 | 0.57 | 0.025181 |  | 1.396 |  | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03014021 | 12 | 55 | 21 | 8.6 | 5732 | 1248 | 0.57 | 0.037263 |  | 1.468 |  | 2727 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03016010 | 12 | 63 | 10 | 4.6 | 2839 | 541 | 0.28 | 0.0099346 |  | 1.403 |  | 1322 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03016011 | 12 | 63 | 11 | 4.6 | 3806 | 725 | 0.38 | 0.031233 |  | 1.44 |  | 1794 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03016015 | 12 | 63 | 15 | 6.6 | 4679 | 891 | 0.47 | 0.023435 |  | 1.396 |  | 2174 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03016016 | 12 | 63 | 16 | 6.6 | 4997 | 952 | 0.5 | 0.072587 |  | 1.456 |  | 2368 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03016020 | 12 | 63 | 20 | 8.6 | 6565 | 1251 | 0.66 | 0.034448 |  | 1.396 |  | 3050 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03016021 | 12 | 63 | 21 | 8.6 | 6552 | 1248 | 0.66 | 0.051335 |  | 1.468 |  | 3117 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03018010 | 12 | 71 | 10 | 4.6 | 3193 | 541 | 0.32 | 0.013624 |  | 1.403 |  | 1487 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03018011 | 12 | 71 | 11 | 4.6 | 4281 | 725 | 0.43 | 0.042216 |  | 1.44 |  | 2018 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03018015 | 12 | 71 | 15 | 6.6 | 5265 | 892 | 0.53 | 0.030594 |  | 1.396 |  | 2446 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03018016 | 12 | 71 | 16 | 6.6 | 5622 | 952 | 0.56 | 0.092832 |  | 1.456 |  | 2664 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03018020 | 12 | 71 | 20 | 8.6 | 7385 | 1251 | 0.74 | 0.044172 |  | 1.396 |  | 3431 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03018021 | 12 | 71 | 21 | 8.6 | 7369 | 1248 | 0.74 | 0.066268 |  | 1.468 |  | 3506 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03020010 | 12 | 78.5 | 10 | 4.6 | 3548 | 541 | 0.35 | 0.017121 |  | 1.403 |  | 1652 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03020011 | 12 | 78.5 | 11 | 4.6 | 4756 | 725 | 0.48 | 0.055285 |  | 1.44 |  | 2242 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03020015 | 12 | 78.5 | 15 | 6.6 | 5850 | 892 | 0.59 | 0.038864 |  | 1.396 |  | 2718 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03020016 | 12 | 78.5 | 16 | 6.6 | 6246 | 952 | 0.62 | 0.1159 |  | 1.456 |  | 2960 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03020020 | 12 | 78.5 | 20 | 8.6 | 8205 | 1250 | 0.82 | 0.055268 |  | 1.396 |  | 3812 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03020021 | 12 | 78.5 | 21 | 8.6 | 8189 | 1248 | 0.82 | 0.083428 |  | 1.468 |  | 3896 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03022010 | 12 | 86.5 | 10 | 4.6 | 3902 | 541 | 0.39 | 0.022162 |  | 1.403 |  | 1817 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03022011 | 12 | 86.5 | 11 | 4.6 | 5231 | 725 | 0.52 | 0.068152 |  | 1.44 |  | 2466 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03022015 | 12 | 86.5 | 15 | 6.6 | 6436 | 892 | 0.64 | 0.04688 |  | 1.396 |  | 2990 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03022016 | 12 | 86.5 | 16 | 6.6 | 6871 | 952 | 0.69 | 0.14594 |  | 1.456 |  | 3256 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03022020 | 12 | 86.5 | 20 | 8.6 | 9025 | 1250 | 0.9 | 0.06778 |  | 1.396 |  | 4193 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03022021 | 12 | 86.5 | 21 | 8.6 | 9009 | 1248 | 0.9 | 0.1029 |  | 1.468 |  | 4286 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03024010 | 12 | 94.5 | 10 | 4.6 | 4256 | 541 | 0.43 | 0.028012 |  | 1.403 |  | 1982 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03024011 | 12 | 94.5 | 11 | 4.6 | 5707 | 725 | 0.57 | 0.085461 |  | 1.44 |  | 2690 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03024015 | 12 | 94.5 | 15 | 6.6 | 7021 | 892 | 0.7 | 0.057344 |  | 1.396 |  | 3262 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03024016 | 12 | 94.5 | 16 | 6.6 | 7496 | 952 | 0.75 | 0.17534 |  | 1.456 |  | 3552 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03024020 | 12 | 94.5 | 20 | 8.6 | 9845 | 1250 | 0.98 | 0.081751 |  | 1.396 |  | 4574 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03024021 | 12 | 94.5 | 21 | 8.6 | 9826 | 1248 | 0.98 | 0.12478 |  | 1.468 |  | 4675 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03026010 | 12 | 102.5 | 10 | 4.6 | 4613 | 541 | 0.46 | 0.033371 |  | 1.403 |  | 2148 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03026011 | 12 | 102.5 | 11 | 4.6 | 6184 | 725 | 0.62 | 0.10524 |  | 1.44 |  | 2915 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03026015 | 12 | 102.5 | 15 | 6.6 | 7605 | 892 | 0.76 | 0.069047 |  | 1.396 |  | 3533 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03026016 | 12 | 102.5 | 16 | 6.6 | 8120 | 952 | 0.81 | 0.20783 |  | 1.456 |  | 3848 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03026020 | 12 | 102.5 | 20 | 8.6 | 10667 | 1251 | 1.07 | 0.098998 |  | 1.396 |  | 4956 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03026021 | 12 | 102.5 | 21 | 8.6 | 10646 | 1248 | 1.06 | 0.14915 |  | 1.468 |  | 5065 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03028010 | 12 | 110 | 10 | 4.6 | 4967 | 541 | 0.5 | 0.04081 |  | 1.403 |  | 2313 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03028011 | 12 | 110 | 11 | 4.6 | 6659 | 725 | 0.67 | 0.12762 |  | 1.44 |  | 3139 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03028015 | 12 | 110 | 15 | 6.6 | 8190 | 892 | 0.82 | 0.082031 |  | 1.396 |  | 3805 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03028016 | 12 | 110 | 16 | 6.6 | 8745 | 952 | 0.87 | 0.24349 |  | 1.456 |  | 4144 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03028020 | 12 | 110 | 20 | 8.6 | 11487 | 1250 | 1.15 | 0.11617 |  | 1.396 |  | 5337 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03028021 | 12 | 110 | 21 | 8.6 | 11464 | 1248 | 1.15 | 0.17903 |  | 1.468 |  | 5454 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.03030010 | 12 | 118 | 10 | 4.6 | 5321 | 541 | 0.53 | 0.047527 |  | 1.403 |  | 2478 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.03030011 | 12 | 118 | 11 | 4.6 | 7134 | 725 | 0.71 | 0.14887 |  | 1.44 |  | 3363 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.03030015 | 12 | 118 | 15 | 6.6 | 8775 | 892 | 0.88 | 0.096338 |  | 1.396 |  | 4077 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.03030016 | 12 | 118 | 16 | 6.6 | 9369 | 952 | 0.94 | 0.28828 |  | 1.456 |  | 4440 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.03030020 | 12 | 118 | 20 | 8.6 | 12308 | 1250 | 1.23 | 0.13494 |  | 1.396 |  | 5718 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.03030021 | 12 | 118 | 21 | 8.6 | 12283 | 1248 | 1.23 | 0.20888 |  | 1.468 |  | 5844 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04004010 | 15.5 | 15.5 | 10 | 4.6 | 829 | 632 | 0.08 | 0.00049816 |  | 1.394 |  | 385 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04004011 | 15.5 | 15.5 | 11 | 4.6 | 1074 | 818 | 0.11 | 0.0015251 |  | 1.439 |  | 506 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04004015 | 15.5 | 15.5 | 15 | 6.6 | 1354 | 1032 | 0.14 | 0.0016625 |  | 1.385 |  | 627 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04004016 | 15.5 | 15.5 | 16 | 6.6 | 1433 | 1092 | 0.14 | 0.0048759 |  | 1.46 |  | 680 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04004020 | 15.5 | 15.5 | 20 | 8.6 | 1897 | 1446 | 0.19 | 0.0024328 |  | 1.384 |  | 878 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04004021 | 15.5 | 15.5 | 21 | 8.6 | 1907 | 1453 | 0.19 | 0.0034102 |  | 1.477 |  | 910 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04005010 | 15.5 | 19.5 | 10 | 4.6 | 1038 | 633 | 0.1 | 0.00082769 |  | 1.394 |  | 482 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04005011 | 15.5 | 19.5 | 11 | 4.6 | 1341 | 817 | 0.13 | 0.0022931 |  | 1.439 |  | 632 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04005015 | 15.5 | 19.5 | 15 | 6.6 | 1694 | 1033 | 0.17 | 0.002515 |  | 1.385 |  | 784 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04005016 | 15.5 | 19.5 | 16 | 6.6 | 1791 | 1092 | 0.18 | 0.0081936 |  | 1.46 |  | 850 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04005020 | 15.5 | 19.5 | 20 | 8.6 | 2373 | 1447 | 0.24 | 0.0039492 |  | 1.384 |  | 1098 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04005021 | 15.5 | 19.5 | 21 | 8.6 | 2383 | 1453 | 0.24 | 0.0055763 |  | 1.477 |  | 1137 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04006010 | 15.5 | 23.5 | 10 | 4.6 | 1245 | 632 | 0.12 | 0.0012579 |  | 1.394 |  | 578 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04006011 | 15.5 | 23.5 | 11 | 4.6 | 1609 | 817 | 0.16 | 0.0036844 |  | 1.439 |  | 758 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04006015 | 15.5 | 23.5 | 15 | 6.6 | 2033 | 1033 | 0.2 | 0.0035629 |  | 1.385 |  | 941 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04006016 | 15.5 | 23.5 | 16 | 6.6 | 2150 | 1092 | 0.22 | 0.012424 |  | 1.46 |  | 1020 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04006020 | 15.5 | 23.5 | 20 | 8.6 | 2848 | 1447 | 0.28 | 0.0054651 |  | 1.384 |  | 1318 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04006021 | 15.5 | 23.5 | 21 | 8.6 | 2858 | 1452 | 0.29 | 0.0083243 |  | 1.477 |  | 1364 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04007010 | 15.5 | 27.5 | 10 | 4.6 | 1452 | 632 | 0.15 | 0.0020507 |  | 1.394 |  | 674 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04007011 | 15.5 | 27.5 | 11 | 4.6 | 1878 | 818 | 0.19 | 0.0054758 |  | 1.439 |  | 885 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04007015 | 15.5 | 27.5 | 15 | 6.6 | 2372 | 1033 | 0.24 | 0.0052333 |  | 1.385 |  | 1098 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04007016 | 15.5 | 27.5 | 16 | 6.6 | 2508 | 1092 | 0.25 | 0.016284 |  | 1.46 |  | 1190 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04007020 | 15.5 | 27.5 | 20 | 8.6 | 3321 | 1446 | 0.33 | 0.0077023 |  | 1.384 |  | 1537 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04007021 | 15.5 | 27.5 | 21 | 8.6 | 3336 | 1453 | 0.33 | 0.011014 |  | 1.477 |  | 1592 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04008010 | 15.5 | 31.5 | 10 | 4.6 | 1658 | 632 | 0.17 | 0.0027532 |  | 1.394 |  | 770 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04008011 | 15.5 | 31.5 | 11 | 4.6 | 2145 | 817 | 0.21 | 0.0070493 |  | 1.439 |  | 1011 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04008015 | 15.5 | 31.5 | 15 | 6.6 | 2709 | 1032 | 0.27 | 0.0067576 |  | 1.385 |  | 1254 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04008016 | 15.5 | 31.5 | 16 | 6.6 | 2866 | 1092 | 0.29 | 0.022198 |  | 1.46 |  | 1360 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04008020 | 15.5 | 31.5 | 20 | 8.6 | 3797 | 1447 | 0.38 | 0.010353 |  | 1.384 |  | 1757 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04008021 | 15.5 | 31.5 | 21 | 8.6 | 3812 | 1452 | 0.38 | 0.014884 |  | 1.477 |  | 1819 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04009010 | 15.5 | 35.5 | 10 | 4.6 | 1867 | 632 | 0.19 | 0.0035822 |  | 1.394 |  | 867 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04009011 | 15.5 | 35.5 | 11 | 4.6 | 2415 | 818 | 0.24 | 0.0096146 |  | 1.439 |  | 1138 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04009015 | 15.5 | 35.5 | 15 | 6.6 | 3048 | 1032 | 0.3 | 0.0085018 |  | 1.385 |  | 1411 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04009016 | 15.5 | 35.5 | 16 | 6.6 | 3224 | 1092 | 0.32 | 0.027389 |  | 1.46 |  | 1530 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04009020 | 15.5 | 35.5 | 20 | 8.6 | 4270 | 1446 | 0.43 | 0.013428 |  | 1.384 |  | 1976 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04009021 | 15.5 | 35.5 | 21 | 8.6 | 4290 | 1453 | 0.43 | 0.019402 |  | 1.477 |  | 2047 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04010010 | 15.5 | 39.5 | 10 | 4.6 | 2074 | 632 | 0.21 | 0.0045446 |  | 1.394 |  | 963 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04010011 | 15.5 | 39.5 | 11 | 4.6 | 2682 | 817 | 0.27 | 0.012666 |  | 1.439 |  | 1264 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04010015 | 15.5 | 39.5 | 15 | 6.6 | 3387 | 1032 | 0.34 | 0.0111 |  | 1.385 |  | 1568 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04010016 | 15.5 | 39.5 | 16 | 6.6 | 3583 | 1092 | 0.36 | 0.03507 |  | 1.46 |  | 1700 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04010020 | 15.5 | 39.5 | 20 | 8.6 | 4745 | 1446 | 0.47 | 0.016253 |  | 1.384 |  | 2196 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04010021 | 15.5 | 39.5 | 21 | 8.6 | 4765 | 1452 | 0.48 | 0.024588 |  | 1.477 |  | 2274 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04011010 | 15.5 | 43.5 | 10 | 4.6 | 2281 | 632 | 0.23 | 0.0056475 |  | 1.394 |  | 1059 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04011011 | 15.5 | 43.5 | 11 | 4.6 | 2950 | 817 | 0.3 | 0.016232 |  | 1.439 |  | 1390 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04011015 | 15.5 | 43.5 | 15 | 6.6 | 3726 | 1032 | 0.37 | 0.013371 |  | 1.385 |  | 1725 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04011016 | 15.5 | 43.5 | 16 | 6.6 | 3941 | 1092 | 0.39 | 0.04166 |  | 1.46 |  | 1870 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04011020 | 15.5 | 43.5 | 20 | 8.6 | 5221 | 1447 | 0.52 | 0.020128 |  | 1.384 |  | 2416 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04011021 | 15.5 | 43.5 | 21 | 8.6 | 5241 | 1452 | 0.52 | 0.029356 |  | 1.477 |  | 2501 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04012010 | 15.5 | 47 | 10 | 4.6 | 2490 | 632 | 0.25 | 0.0068976 |  | 1.394 |  | 1156 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04012011 | 15.5 | 47 | 11 | 4.6 | 3219 | 818 | 0.32 | 0.019203 |  | 1.439 |  | 1517 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04012015 | 15.5 | 47 | 15 | 6.6 | 4066 | 1033 | 0.41 | 0.016663 |  | 1.385 |  | 1882 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04012016 | 15.5 | 47 | 16 | 6.6 | 4299 | 1092 | 0.43 | 0.051186 |  | 1.46 |  | 2040 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04012020 | 15.5 | 47 | 20 | 8.6 | 5694 | 1446 | 0.57 | 0.024458 |  | 1.384 |  | 2635 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04012021 | 15.5 | 47 | 21 | 8.6 | 5719 | 1453 | 0.57 | 0.035817 |  | 1.477 |  | 2729 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04014010 | 15.5 | 55 | 10 | 4.6 | 2903 | 632 | 0.29 | 0.0098653 |  | 1.394 |  | 1348 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04014011 | 15.5 | 55 | 11 | 4.6 | 3756 | 818 | 0.38 | 0.028864 |  | 1.439 |  | 1770 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04014015 | 15.5 | 55 | 15 | 6.6 | 4742 | 1032 | 0.47 | 0.022579 |  | 1.385 |  | 2195 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04014016 | 15.5 | 55 | 16 | 6.6 | 5016 | 1092 | 0.5 | 0.070684 |  | 1.46 |  | 2380 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04014020 | 15.5 | 55 | 20 | 8.6 | 6643 | 1446 | 0.66 | 0.033517 |  | 1.384 |  | 3074 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04014021 | 15.5 | 55 | 21 | 8.6 | 6673 | 1453 | 0.67 | 0.050933 |  | 1.477 |  | 3184 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04016010 | 15.5 | 63 | 10 | 4.6 | 3319 | 632 | 0.33 | 0.013499 |  | 1.394 |  | 1541 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04016011 | 15.5 | 63 | 11 | 4.6 | 4291 | 817 | 0.43 | 0.03928 |  | 1.439 |  | 2022 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04016015 | 15.5 | 63 | 15 | 6.6 | 5420 | 1033 | 0.54 | 0.030626 |  | 1.385 |  | 2509 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04016016 | 15.5 | 63 | 16 | 6.6 | 5732 | 1092 | 0.57 | 0.093695 |  | 1.46 |  | 2720 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04016020 | 15.5 | 63 | 20 | 8.6 | 7594 | 1447 | 0.76 | 0.045332 |  | 1.384 |  | 3514 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04016021 | 15.5 | 63 | 21 | 8.6 | 7624 | 1452 | 0.76 | 0.067378 |  | 1.477 |  | 3638 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04018010 | 15.5 | 71 | 10 | 4.6 | 3733 | 632 | 0.37 | 0.017846 |  | 1.394 |  | 1733 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04018011 | 15.5 | 71 | 11 | 4.6 | 4828 | 818 | 0.48 | 0.051733 |  | 1.439 |  | 2275 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04018015 | 15.5 | 71 | 15 | 6.6 | 6096 | 1032 | 0.61 | 0.040087 |  | 1.385 |  | 2822 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04018016 | 15.5 | 71 | 16 | 6.6 | 6449 | 1092 | 0.64 | 0.12034 |  | 1.46 |  | 3060 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04018020 | 15.5 | 71 | 20 | 8.6 | 8542 | 1446 | 0.85 | 0.057812 |  | 1.384 |  | 3953 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04018021 | 15.5 | 71 | 21 | 8.6 | 8577 | 1452 | 0.86 | 0.088465 |  | 1.477 |  | 4093 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04020010 | 15.5 | 78.5 | 10 | 4.6 | 4148 | 632 | 0.41 | 0.022956 |  | 1.394 |  | 1926 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04020011 | 15.5 | 78.5 | 11 | 4.6 | 5365 | 818 | 0.54 | 0.068687 |  | 1.439 |  | 2528 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04020015 | 15.5 | 78.5 | 15 | 6.6 | 6775 | 1033 | 0.68 | 0.051025 |  | 1.385 |  | 3136 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04020016 | 15.5 | 78.5 | 16 | 6.6 | 7165 | 1092 | 0.72 | 0.1549 |  | 1.46 |  | 3400 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04020020 | 15.5 | 78.5 | 20 | 8.6 | 9491 | 1446 | 0.95 | 0.073505 |  | 1.384 |  | 4392 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04020021 | 15.5 | 78.5 | 21 | 8.6 | 9531 | 1453 | 0.95 | 0.11063 |  | 1.477 |  | 4548 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04022010 | 15.5 | 86.5 | 10 | 4.6 | 4564 | 632 | 0.46 | 0.030071 |  | 1.394 |  | 2119 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04022011 | 15.5 | 86.5 | 11 | 4.6 | 5902 | 818 | 0.59 | 0.085955 |  | 1.439 |  | 2781 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04022015 | 15.5 | 86.5 | 15 | 6.6 | 7453 | 1033 | 0.75 | 0.063499 |  | 1.385 |  | 3450 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04022016 | 15.5 | 86.5 | 16 | 6.6 | 7882 | 1092 | 0.79 | 0.18967 |  | 1.46 |  | 3740 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04022020 | 15.5 | 86.5 | 20 | 8.6 | 10440 | 1446 | 1.04 | 0.089647 |  | 1.384 |  | 4831 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04022021 | 15.5 | 86.5 | 21 | 8.6 | 10485 | 1453 | 1.05 | 0.1382 |  | 1.477 |  | 5003 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04024010 | 15.5 | 94.5 | 10 | 4.6 | 4978 | 632 | 0.5 | 0.036997 |  | 1.394 |  | 2311 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04024011 | 15.5 | 94.5 | 11 | 4.6 | 6438 | 818 | 0.64 | 0.10568 |  | 1.439 |  | 3034 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04024015 | 15.5 | 94.5 | 15 | 6.6 | 8129 | 1032 | 0.81 | 0.075768 |  | 1.385 |  | 3763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04024016 | 15.5 | 94.5 | 16 | 6.6 | 8598 | 1092 | 0.86 | 0.22844 |  | 1.46 |  | 4080 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04024020 | 15.5 | 94.5 | 20 | 8.6 | 11388 | 1446 | 1.14 | 0.10947 |  | 1.384 |  | 5270 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04024021 | 15.5 | 94.5 | 21 | 8.6 | 11438 | 1453 | 1.14 | 0.16654 |  | 1.477 |  | 5458 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04026010 | 15.5 | 102.5 | 10 | 4.6 | 5393 | 632 | 0.54 | 0.044825 |  | 1.394 |  | 2504 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04026011 | 15.5 | 102.5 | 11 | 4.6 | 6973 | 817 | 0.7 | 0.1314 |  | 1.439 |  | 3286 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04026015 | 15.5 | 102.5 | 15 | 6.6 | 8807 | 1032 | 0.88 | 0.091294 |  | 1.385 |  | 4077 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04026016 | 15.5 | 102.5 | 16 | 6.6 | 9315 | 1092 | 0.93 | 0.27132 |  | 1.46 |  | 4420 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04026020 | 15.5 | 102.5 | 20 | 8.6 | 12339 | 1447 | 1.23 | 0.1295 |  | 1.384 |  | 5710 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04026021 | 15.5 | 102.5 | 21 | 8.6 | 12389 | 1452 | 1.24 | 0.20108 |  | 1.477 |  | 5912 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04028010 | 15.5 | 110 | 10 | 4.6 | 5807 | 632 | 0.58 | 0.053598 |  | 1.394 |  | 2696 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04028011 | 15.5 | 110 | 11 | 4.6 | 7510 | 818 | 0.75 | 0.1568 |  | 1.439 |  | 3539 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04028015 | 15.5 | 110 | 15 | 6.6 | 9484 | 1032 | 0.95 | 0.10852 |  | 1.385 |  | 4390 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04028016 | 15.5 | 110 | 16 | 6.6 | 10031 | 1092 | 1 | 0.31842 |  | 1.46 |  | 4760 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04028020 | 15.5 | 110 | 20 | 8.6 | 13288 | 1446 | 1.33 | 0.15368 |  | 1.384 |  | 6149 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04028021 | 15.5 | 110 | 21 | 8.6 | 13343 | 1452 | 1.33 | 0.23605 |  | 1.477 |  | 6367 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.04030010 | 15.5 | 118 | 10 | 4.6 | 6222 | 632 | 0.62 | 0.063358 |  | 1.394 |  | 2889 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.04030011 | 15.5 | 118 | 11 | 4.6 | 8047 | 818 | 0.8 | 0.18505 |  | 1.439 |  | 3792 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.04030015 | 15.5 | 118 | 15 | 6.6 | 10162 | 1032 | 1.02 | 0.1275 |  | 1.385 |  | 4704 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.04030016 | 15.5 | 118 | 16 | 6.6 | 10748 | 1092 | 1.07 | 0.36986 |  | 1.46 |  | 5100 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.04030020 | 15.5 | 118 | 20 | 8.6 | 14236 | 1446 | 1.42 | 0.17782 |  | 1.384 |  | 6588 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.04030021 | 15.5 | 118 | 21 | 8.6 | 14296 | 1452 | 1.43 | 0.27803 |  | 1.477 |  | 6822 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05004010 | 19.5 | 15.5 | 10 | 4.6 | 929 | 708 | 0.09 | 0.00062652 |  | 1.385 |  | 430 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05004011 | 19.5 | 15.5 | 11 | 4.6 | 1176 | 896 | 0.12 | 0.0018055 |  | 1.438 |  | 554 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05004015 | 19.5 | 15.5 | 15 | 6.6 | 1505 | 1147 | 0.15 | 0.0019055 |  | 1.373 |  | 694 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05004016 | 19.5 | 15.5 | 16 | 6.6 | 1597 | 1217 | 0.16 | 0.0063557 |  | 1.464 |  | 759 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05004020 | 19.5 | 15.5 | 20 | 8.6 | 2104 | 1603 | 0.21 | 0.0029673 |  | 1.373 |  | 970 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05004021 | 19.5 | 15.5 | 21 | 8.6 | 2159 | 1645 | 0.22 | 0.0045572 |  | 1.485 |  | 1033 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05005010 | 19.5 | 19.5 | 10 | 4.6 | 1162 | 708 | 0.12 | 0.0011777 |  | 1.385 |  | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05005011 | 19.5 | 19.5 | 11 | 4.6 | 1471 | 897 | 0.15 | 0.0030203 |  | 1.438 |  | 693 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05005015 | 19.5 | 19.5 | 15 | 6.6 | 1880 | 1146 | 0.19 | 0.0031316 |  | 1.373 |  | 867 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05005016 | 19.5 | 19.5 | 16 | 6.6 | 1997 | 1217 | 0.2 | 0.010095 |  | 1.464 |  | 949 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05005020 | 19.5 | 19.5 | 20 | 8.6 | 2631 | 1604 | 0.26 | 0.0046274 |  | 1.373 |  | 1213 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05005021 | 19.5 | 19.5 | 21 | 8.6 | 2698 | 1645 | 0.27 | 0.0070338 |  | 1.485 |  | 1291 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05006010 | 19.5 | 23.5 | 10 | 4.6 | 1396 | 709 | 0.14 | 0.0016922 |  | 1.385 |  | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05006011 | 19.5 | 23.5 | 11 | 4.6 | 1766 | 897 | 0.18 | 0.0046161 |  | 1.438 |  | 832 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05006015 | 19.5 | 23.5 | 15 | 6.6 | 2256 | 1146 | 0.23 | 0.0046896 |  | 1.373 |  | 1040 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05006016 | 19.5 | 23.5 | 16 | 6.6 | 2397 | 1218 | 0.24 | 0.014756 |  | 1.464 |  | 1139 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05006020 | 19.5 | 23.5 | 20 | 8.6 | 3156 | 1603 | 0.32 | 0.007115 |  | 1.373 |  | 1455 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05006021 | 19.5 | 23.5 | 21 | 8.6 | 3238 | 1645 | 0.32 | 0.010102 |  | 1.485 |  | 1549 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05007010 | 19.5 | 27.5 | 10 | 4.6 | 1627 | 708 | 0.16 | 0.0023206 |  | 1.385 |  | 753 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05007011 | 19.5 | 27.5 | 11 | 4.6 | 2059 | 897 | 0.21 | 0.0066259 |  | 1.438 |  | 970 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05007015 | 19.5 | 27.5 | 15 | 6.6 | 2633 | 1146 | 0.26 | 0.0061227 |  | 1.373 |  | 1214 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05007016 | 19.5 | 27.5 | 16 | 6.6 | 2797 | 1218 | 0.28 | 0.020365 |  | 1.464 |  | 1329 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05007020 | 19.5 | 27.5 | 20 | 8.6 | 3683 | 1604 | 0.37 | 0.0096517 |  | 1.373 |  | 1698 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05007021 | 19.5 | 27.5 | 21 | 8.6 | 3777 | 1645 | 0.38 | 0.014525 |  | 1.485 |  | 1807 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05008010 | 19.5 | 31.5 | 10 | 4.6 | 1860 | 709 | 0.19 | 0.0034042 |  | 1.385 |  | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05008011 | 19.5 | 31.5 | 11 | 4.6 | 2354 | 897 | 0.24 | 0.0090809 |  | 1.438 |  | 1109 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05008015 | 19.5 | 31.5 | 15 | 6.6 | 3008 | 1146 | 0.3 | 0.0083046 |  | 1.373 |  | 1387 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05008016 | 19.5 | 31.5 | 16 | 6.6 | 3195 | 1217 | 0.32 | 0.026948 |  | 1.464 |  | 1518 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05008020 | 19.5 | 31.5 | 20 | 8.6 | 4208 | 1603 | 0.42 | 0.012608 |  | 1.373 |  | 1940 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05008021 | 19.5 | 31.5 | 21 | 8.6 | 4318 | 1645 | 0.43 | 0.018957 |  | 1.485 |  | 2066 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05009010 | 19.5 | 35.5 | 10 | 4.6 | 2091 | 708 | 0.21 | 0.0043329 |  | 1.385 |  | 968 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05009011 | 19.5 | 35.5 | 11 | 4.6 | 2647 | 896 | 0.26 | 0.011184 |  | 1.438 |  | 1247 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05009015 | 19.5 | 35.5 | 15 | 6.6 | 3386 | 1147 | 0.34 | 0.010855 |  | 1.373 |  | 1561 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05009016 | 19.5 | 35.5 | 16 | 6.6 | 3595 | 1218 | 0.36 | 0.03453 |  | 1.464 |  | 1708 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05009020 | 19.5 | 35.5 | 20 | 8.6 | 4735 | 1604 | 0.47 | 0.015994 |  | 1.373 |  | 2183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05009021 | 19.5 | 35.5 | 21 | 8.6 | 4857 | 1645 | 0.49 | 0.025038 |  | 1.485 |  | 2324 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05010010 | 19.5 | 39.5 | 10 | 4.6 | 2324 | 708 | 0.23 | 0.0053996 |  | 1.385 |  | 1076 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05010011 | 19.5 | 39.5 | 11 | 4.6 | 2942 | 897 | 0.29 | 0.014491 |  | 1.438 |  | 1386 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05010015 | 19.5 | 39.5 | 15 | 6.6 | 3761 | 1146 | 0.38 | 0.013786 |  | 1.373 |  | 1734 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05010016 | 19.5 | 39.5 | 16 | 6.6 | 3995 | 1218 | 0.4 | 0.043132 |  | 1.464 |  | 1898 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05010020 | 19.5 | 39.5 | 20 | 8.6 | 5259 | 1603 | 0.53 | 0.020575 |  | 1.373 |  | 2425 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05010021 | 19.5 | 39.5 | 21 | 8.6 | 5397 | 1645 | 0.54 | 0.030932 |  | 1.485 |  | 2582 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05011010 | 19.5 | 43.5 | 10 | 4.6 | 2558 | 709 | 0.26 | 0.0071199 |  | 1.385 |  | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05011011 | 19.5 | 43.5 | 11 | 4.6 | 3237 | 897 | 0.32 | 0.018324 |  | 1.438 |  | 1525 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05011015 | 19.5 | 43.5 | 15 | 6.6 | 4136 | 1146 | 0.41 | 0.016325 |  | 1.373 |  | 1907 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05011016 | 19.5 | 43.5 | 16 | 6.6 | 4395 | 1218 | 0.44 | 0.05278 |  | 1.464 |  | 2088 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05011020 | 19.5 | 43.5 | 20 | 8.6 | 5786 | 1603 | 0.58 | 0.024932 |  | 1.373 |  | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05011021 | 19.5 | 43.5 | 21 | 8.6 | 5936 | 1645 | 0.59 | 0.037529 |  | 1.485 |  | 2840 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05012010 | 19.5 | 47 | 10 | 4.6 | 2789 | 708 | 0.28 | 0.0085399 |  | 1.385 |  | 1291 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05012011 | 19.5 | 47 | 11 | 4.6 | 3530 | 897 | 0.35 | 0.022711 |  | 1.438 |  | 1663 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05012015 | 19.5 | 47 | 15 | 6.6 | 4513 | 1146 | 0.45 | 0.019964 |  | 1.373 |  | 2081 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05012016 | 19.5 | 47 | 16 | 6.6 | 4794 | 1218 | 0.48 | 0.063493 |  | 1.464 |  | 2278 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05012020 | 19.5 | 47 | 20 | 8.6 | 6311 | 1603 | 0.63 | 0.02975 |  | 1.373 |  | 2910 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05012021 | 19.5 | 47 | 21 | 8.6 | 6475 | 1645 | 0.65 | 0.04622 |  | 1.485 |  | 3098 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05014010 | 19.5 | 55 | 10 | 4.6 | 3253 | 708 | 0.33 | 0.012571 |  | 1.385 |  | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05014011 | 19.5 | 55 | 11 | 4.6 | 4118 | 897 | 0.41 | 0.033256 |  | 1.438 |  | 1940 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05014015 | 19.5 | 55 | 15 | 6.6 | 5266 | 1146 | 0.53 | 0.028489 |  | 1.373 |  | 2428 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05014016 | 19.5 | 55 | 16 | 6.6 | 5592 | 1217 | 0.56 | 0.088204 |  | 1.464 |  | 2657 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05014020 | 19.5 | 55 | 20 | 8.6 | 7363 | 1603 | 0.74 | 0.041905 |  | 1.373 |  | 3395 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05014021 | 19.5 | 55 | 21 | 8.6 | 7556 | 1645 | 0.76 | 0.065004 |  | 1.485 |  | 3615 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05016010 | 19.5 | 63 | 10 | 4.6 | 3720 | 709 | 0.37 | 0.016715 |  | 1.385 |  | 1722 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05016011 | 19.5 | 63 | 11 | 4.6 | 4708 | 897 | 0.47 | 0.046333 |  | 1.438 |  | 2218 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05016015 | 19.5 | 63 | 15 | 6.6 | 6016 | 1146 | 0.6 | 0.03753 |  | 1.373 |  | 2774 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05016016 | 19.5 | 63 | 16 | 6.6 | 6392 | 1218 | 0.64 | 0.11743 |  | 1.464 |  | 3037 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05016020 | 19.5 | 63 | 20 | 8.6 | 8415 | 1603 | 0.84 | 0.055088 |  | 1.373 |  | 3880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05016021 | 19.5 | 63 | 21 | 8.6 | 8634 | 1645 | 0.86 | 0.085528 |  | 1.485 |  | 4131 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05018010 | 19.5 | 71 | 10 | 4.6 | 4184 | 708 | 0.42 | 0.022597 |  | 1.385 |  | 1937 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05018011 | 19.5 | 71 | 11 | 4.6 | 5296 | 897 | 0.53 | 0.062141 |  | 1.438 |  | 2495 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05018015 | 19.5 | 71 | 15 | 6.6 | 6769 | 1146 | 0.68 | 0.049408 |  | 1.373 |  | 3121 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05018016 | 19.5 | 71 | 16 | 6.6 | 7190 | 1218 | 0.72 | 0.15133 |  | 1.464 |  | 3416 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05018020 | 19.5 | 71 | 20 | 8.6 | 9467 | 1603 | 0.95 | 0.071762 |  | 1.373 |  | 4365 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05018021 | 19.5 | 71 | 21 | 8.6 | 9715 | 1645 | 0.97 | 0.11152 |  | 1.485 |  | 4648 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05020010 | 19.5 | 78.5 | 10 | 4.6 | 4649 | 709 | 0.46 | 0.028422 |  | 1.385 |  | 2152 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05020011 | 19.5 | 78.5 | 11 | 4.6 | 5884 | 897 | 0.59 | 0.080874 |  | 1.438 |  | 2772 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05020015 | 19.5 | 78.5 | 15 | 6.6 | 7521 | 1146 | 0.75 | 0.061584 |  | 1.373 |  | 3468 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05020016 | 19.5 | 78.5 | 16 | 6.6 | 7989 | 1218 | 0.8 | 0.19007 |  | 1.464 |  | 3796 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05020020 | 19.5 | 78.5 | 20 | 8.6 | 10519 | 1603 | 1.05 | 0.089252 |  | 1.373 |  | 4850 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05020021 | 19.5 | 78.5 | 21 | 8.6 | 10793 | 1645 | 1.08 | 0.14151 |  | 1.485 |  | 5164 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05022010 | 19.5 | 86.5 | 10 | 4.6 | 5113 | 708 | 0.51 | 0.036401 |  | 1.385 |  | 2367 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05022011 | 19.5 | 86.5 | 11 | 4.6 | 6472 | 897 | 0.65 | 0.10272 |  | 1.438 |  | 3049 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05022015 | 19.5 | 86.5 | 15 | 6.6 | 8274 | 1146 | 0.83 | 0.077102 |  | 1.373 |  | 3815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05022016 | 19.5 | 86.5 | 16 | 6.6 | 8789 | 1218 | 0.88 | 0.23378 |  | 1.464 |  | 4176 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05022020 | 19.5 | 86.5 | 20 | 8.6 | 11571 | 1603 | 1.16 | 0.11075 |  | 1.373 |  | 5335 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05022021 | 19.5 | 86.5 | 21 | 8.6 | 11872 | 1645 | 1.19 | 0.17564 |  | 1.485 |  | 5680 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05024010 | 19.5 | 94.5 | 10 | 4.6 | 5578 | 708 | 0.56 | 0.045609 |  | 1.385 |  | 2582 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05024011 | 19.5 | 94.5 | 11 | 4.6 | 7060 | 897 | 0.71 | 0.12785 |  | 1.438 |  | 3326 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05024015 | 19.5 | 94.5 | 15 | 6.6 | 9027 | 1146 | 0.9 | 0.092669 |  | 1.373 |  | 4162 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05024016 | 19.5 | 94.5 | 16 | 6.6 | 9587 | 1218 | 0.96 | 0.28261 |  | 1.464 |  | 4555 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05024020 | 19.5 | 94.5 | 20 | 8.6 | 12623 | 1603 | 1.26 | 0.13282 |  | 1.373 |  | 5820 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05024021 | 19.5 | 94.5 | 21 | 8.6 | 12952 | 1645 | 1.3 | 0.21406 |  | 1.485 |  | 6197 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05026010 | 19.5 | 102.5 | 10 | 4.6 | 6044 | 709 | 0.6 | 0.054428 |  | 1.385 |  | 2798 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05026011 | 19.5 | 102.5 | 11 | 4.6 | 7651 | 897 | 0.77 | 0.15646 |  | 1.438 |  | 3604 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05026015 | 19.5 | 102.5 | 15 | 6.6 | 9777 | 1146 | 0.98 | 0.1121 |  | 1.373 |  | 4508 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05026016 | 19.5 | 102.5 | 16 | 6.6 | 10386 | 1218 | 1.04 | 0.33671 |  | 1.464 |  | 4935 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05026020 | 19.5 | 102.5 | 20 | 8.6 | 13674 | 1603 | 1.37 | 0.15943 |  | 1.373 |  | 6305 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05026021 | 19.5 | 102.5 | 21 | 8.6 | 14031 | 1645 | 1.4 | 0.25346 |  | 1.485 |  | 6713 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05028010 | 19.5 | 110 | 10 | 4.6 | 6509 | 709 | 0.65 | 0.066091 |  | 1.385 |  | 3013 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05028011 | 19.5 | 110 | 11 | 4.6 | 8239 | 897 | 0.82 | 0.18457 |  | 1.438 |  | 3881 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05028015 | 19.5 | 110 | 15 | 6.6 | 10530 | 1146 | 1.05 | 0.1313 |  | 1.373 |  | 4855 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05028016 | 19.5 | 110 | 16 | 6.6 | 11184 | 1217 | 1.12 | 0.39621 |  | 1.464 |  | 5314 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05028020 | 19.5 | 110 | 20 | 8.6 | 14726 | 1603 | 1.47 | 0.18636 |  | 1.373 |  | 6790 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05028021 | 19.5 | 110 | 21 | 8.6 | 15112 | 1645 | 1.51 | 0.30058 |  | 1.485 |  | 7230 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.05030010 | 19.5 | 118 | 10 | 4.6 | 6973 | 708 | 0.7 | 0.079166 |  | 1.385 |  | 3228 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.05030011 | 19.5 | 118 | 11 | 4.6 | 8827 | 897 | 0.88 | 0.22019 |  | 1.438 |  | 4158 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.05030015 | 19.5 | 118 | 15 | 6.6 | 11282 | 1146 | 1.13 | 0.15489 |  | 1.373 |  | 5202 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.05030016 | 19.5 | 118 | 16 | 6.6 | 11984 | 1218 | 1.2 | 0.46124 |  | 1.464 |  | 5694 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.05030020 | 19.5 | 118 | 20 | 8.6 | 15778 | 1603 | 1.58 | 0.21835 |  | 1.373 |  | 7275 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.05030021 | 19.5 | 118 | 21 | 8.6 | 16190 | 1645 | 1.62 | 0.35241 |  | 1.485 |  | 7746 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06004010 | 23.5 | 15.5 | 10 | 4.6 | 1014 | 773 | 0.1 | 0.00076924 |  | 1.376 |  | 468 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06004011 | 23.5 | 15.5 | 11 | 4.6 | 1270 | 968 | 0.13 | 0.0021088 |  | 1.437 |  | 598 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06004015 | 23.5 | 15.5 | 15 | 6.6 | 1624 | 1237 | 0.16 | 0.002165 |  | 1.361 |  | 746 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06004016 | 23.5 | 15.5 | 16 | 6.6 | 1753 | 1336 | 0.18 | 0.0080301 |  | 1.468 |  | 834 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06004020 | 23.5 | 15.5 | 20 | 8.6 | 2271 | 1731 | 0.23 | 0.0035544 |  | 1.361 |  | 1043 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06004021 | 23.5 | 15.5 | 21 | 8.6 | 2404 | 1832 | 0.24 | 0.0054132 |  | 1.493 |  | 1153 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06005010 | 23.5 | 19.5 | 10 | 4.6 | 1268 | 773 | 0.13 | 0.0013751 |  | 1.376 |  | 585 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06005011 | 23.5 | 19.5 | 11 | 4.6 | 1586 | 967 | 0.16 | 0.0034202 |  | 1.437 |  | 747 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06005015 | 23.5 | 19.5 | 15 | 6.6 | 2032 | 1239 | 0.2 | 0.0034649 |  | 1.361 |  | 933 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06005016 | 23.5 | 19.5 | 16 | 6.6 | 2190 | 1335 | 0.22 | 0.012193 |  | 1.468 |  | 1042 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06005020 | 23.5 | 19.5 | 20 | 8.6 | 2839 | 1731 | 0.28 | 0.0053588 |  | 1.361 |  | 1304 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06005021 | 23.5 | 19.5 | 21 | 8.6 | 3004 | 1831 | 0.3 | 0.0086584 |  | 1.493 |  | 1441 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06006010 | 23.5 | 23.5 | 10 | 4.6 | 1521 | 773 | 0.15 | 0.0019326 |  | 1.376 |  | 702 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06006011 | 23.5 | 23.5 | 11 | 4.6 | 1903 | 967 | 0.19 | 0.0051198 |  | 1.437 |  | 896 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06006015 | 23.5 | 23.5 | 15 | 6.6 | 2439 | 1239 | 0.24 | 0.005099 |  | 1.361 |  | 1120 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06006016 | 23.5 | 23.5 | 16 | 6.6 | 2627 | 1335 | 0.26 | 0.017286 |  | 1.468 |  | 1250 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06006020 | 23.5 | 23.5 | 20 | 8.6 | 3408 | 1731 | 0.34 | 0.0080207 |  | 1.361 |  | 1565 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06006021 | 23.5 | 23.5 | 21 | 8.6 | 3604 | 1831 | 0.36 | 0.012735 |  | 1.493 |  | 1729 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06007010 | 23.5 | 27.5 | 10 | 4.6 | 1775 | 773 | 0.18 | 0.0029084 |  | 1.376 |  | 819 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06007011 | 23.5 | 27.5 | 11 | 4.6 | 2221 | 967 | 0.22 | 0.0072402 |  | 1.437 |  | 1046 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06007015 | 23.5 | 27.5 | 15 | 6.6 | 2844 | 1238 | 0.28 | 0.0070808 |  | 1.361 |  | 1306 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06007016 | 23.5 | 27.5 | 16 | 6.6 | 3067 | 1335 | 0.31 | 0.024897 |  | 1.468 |  | 1459 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06007020 | 23.5 | 27.5 | 20 | 8.6 | 3976 | 1731 | 0.4 | 0.011256 |  | 1.361 |  | 1826 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06007021 | 23.5 | 27.5 | 21 | 8.6 | 4205 | 1831 | 0.42 | 0.017676 |  | 1.493 |  | 2017 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06008010 | 23.5 | 31.5 | 10 | 4.6 | 2028 | 773 | 0.2 | 0.0037545 |  | 1.376 |  | 936 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06008011 | 23.5 | 31.5 | 11 | 4.6 | 2538 | 967 | 0.25 | 0.0098125 |  | 1.437 |  | 1195 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06008015 | 23.5 | 31.5 | 15 | 6.6 | 3251 | 1239 | 0.33 | 0.010008 |  | 1.361 |  | 1493 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06008016 | 23.5 | 31.5 | 16 | 6.6 | 3504 | 1335 | 0.35 | 0.032154 |  | 1.468 |  | 1667 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06008020 | 23.5 | 31.5 | 20 | 8.6 | 4542 | 1731 | 0.45 | 0.014443 |  | 1.361 |  | 2086 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06008021 | 23.5 | 31.5 | 21 | 8.6 | 4807 | 1831 | 0.48 | 0.023512 |  | 1.493 |  | 2306 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06009010 | 23.5 | 35.5 | 10 | 4.6 | 2282 | 773 | 0.23 | 0.0051517 |  | 1.376 |  | 1053 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06009011 | 23.5 | 35.5 | 11 | 4.6 | 2856 | 967 | 0.29 | 0.013749 |  | 1.437 |  | 1345 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06009015 | 23.5 | 35.5 | 15 | 6.6 | 3656 | 1238 | 0.37 | 0.012805 |  | 1.361 |  | 1679 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06009016 | 23.5 | 35.5 | 16 | 6.6 | 3943 | 1335 | 0.39 | 0.04042 |  | 1.468 |  | 1876 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06009020 | 23.5 | 35.5 | 20 | 8.6 | 5110 | 1731 | 0.51 | 0.01878 |  | 1.361 |  | 2347 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06009021 | 23.5 | 35.5 | 21 | 8.6 | 5407 | 1831 | 0.54 | 0.030273 |  | 1.493 |  | 2594 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06010010 | 23.5 | 39.5 | 10 | 4.6 | 2535 | 773 | 0.25 | 0.0063246 |  | 1.376 |  | 1170 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06010011 | 23.5 | 39.5 | 11 | 4.6 | 3173 | 967 | 0.32 | 0.017445 |  | 1.437 |  | 1494 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06010015 | 23.5 | 39.5 | 15 | 6.6 | 4063 | 1238 | 0.41 | 0.015987 |  | 1.361 |  | 1866 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06010016 | 23.5 | 39.5 | 16 | 6.6 | 4380 | 1335 | 0.44 | 0.052016 |  | 1.468 |  | 2084 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06010020 | 23.5 | 39.5 | 20 | 8.6 | 5679 | 1731 | 0.57 | 0.023734 |  | 1.361 |  | 2608 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06010021 | 23.5 | 39.5 | 21 | 8.6 | 6008 | 1831 | 0.6 | 0.037986 |  | 1.493 |  | 2882 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06011010 | 23.5 | 43.5 | 10 | 4.6 | 2789 | 773 | 0.28 | 0.0081912 |  | 1.376 |  | 1287 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06011011 | 23.5 | 43.5 | 11 | 4.6 | 3489 | 967 | 0.35 | 0.021684 |  | 1.437 |  | 1643 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06011015 | 23.5 | 43.5 | 15 | 6.6 | 4470 | 1239 | 0.45 | 0.019567 |  | 1.361 |  | 2053 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06011016 | 23.5 | 43.5 | 16 | 6.6 | 4818 | 1335 | 0.48 | 0.062606 |  | 1.468 |  | 2292 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06011020 | 23.5 | 43.5 | 20 | 8.6 | 6247 | 1731 | 0.62 | 0.028414 |  | 1.361 |  | 2869 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06011021 | 23.5 | 43.5 | 21 | 8.6 | 6608 | 1831 | 0.66 | 0.04668 |  | 1.493 |  | 3170 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06012010 | 23.5 | 47 | 10 | 4.6 | 3042 | 773 | 0.3 | 0.0097267 |  | 1.376 |  | 1404 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06012011 | 23.5 | 47 | 11 | 4.6 | 3807 | 967 | 0.38 | 0.026495 |  | 1.437 |  | 1793 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06012015 | 23.5 | 47 | 15 | 6.6 | 4875 | 1238 | 0.49 | 0.023556 |  | 1.361 |  | 2239 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06012016 | 23.5 | 47 | 16 | 6.6 | 5257 | 1335 | 0.53 | 0.077101 |  | 1.468 |  | 2501 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06012020 | 23.5 | 47 | 20 | 8.6 | 6815 | 1731 | 0.68 | 0.034548 |  | 1.361 |  | 3130 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06012021 | 23.5 | 47 | 21 | 8.6 | 7209 | 1831 | 0.72 | 0.056381 |  | 1.493 |  | 3458 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06014010 | 23.5 | 55 | 10 | 4.6 | 3549 | 773 | 0.35 | 0.01404 |  | 1.376 |  | 1638 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06014011 | 23.5 | 55 | 11 | 4.6 | 4442 | 967 | 0.44 | 0.037938 |  | 1.437 |  | 2092 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06014015 | 23.5 | 55 | 15 | 6.6 | 5687 | 1238 | 0.57 | 0.0328 |  | 1.361 |  | 2612 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06014016 | 23.5 | 55 | 16 | 6.6 | 6133 | 1335 | 0.61 | 0.10426 |  | 1.468 |  | 2918 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06014020 | 23.5 | 55 | 20 | 8.6 | 7950 | 1731 | 0.8 | 0.048797 |  | 1.361 |  | 3651 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06014021 | 23.5 | 55 | 21 | 8.6 | 8411 | 1831 | 0.84 | 0.078909 |  | 1.493 |  | 4035 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06016010 | 23.5 | 63 | 10 | 4.6 | 4056 | 773 | 0.41 | 0.020253 |  | 1.376 |  | 1872 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06016011 | 23.5 | 63 | 11 | 4.6 | 5075 | 967 | 0.51 | 0.053925 |  | 1.437 |  | 2390 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06016015 | 23.5 | 63 | 15 | 6.6 | 6502 | 1239 | 0.65 | 0.043802 |  | 1.361 |  | 2986 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06016016 | 23.5 | 63 | 16 | 6.6 | 7008 | 1335 | 0.7 | 0.13986 |  | 1.468 |  | 3334 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06016020 | 23.5 | 63 | 20 | 8.6 | 9086 | 1731 | 0.91 | 0.064387 |  | 1.361 |  | 4173 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06016021 | 23.5 | 63 | 21 | 8.6 | 9612 | 1831 | 0.96 | 0.10577 |  | 1.493 |  | 4611 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06018010 | 23.5 | 71 | 10 | 4.6 | 4563 | 773 | 0.46 | 0.026772 |  | 1.376 |  | 2106 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06018011 | 23.5 | 71 | 11 | 4.6 | 5710 | 967 | 0.57 | 0.071102 |  | 1.437 |  | 2689 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06018015 | 23.5 | 71 | 15 | 6.6 | 7314 | 1239 | 0.73 | 0.056642 |  | 1.361 |  | 3359 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06018016 | 23.5 | 71 | 16 | 6.6 | 7884 | 1335 | 0.79 | 0.18129 |  | 1.468 |  | 3751 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06018020 | 23.5 | 71 | 20 | 8.6 | 10221 | 1731 | 1.02 | 0.082402 |  | 1.361 |  | 4694 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06018021 | 23.5 | 71 | 21 | 8.6 | 10815 | 1831 | 1.08 | 0.13716 |  | 1.493 |  | 5188 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06020010 | 23.5 | 78.5 | 10 | 4.6 | 5070 | 773 | 0.51 | 0.034428 |  | 1.376 |  | 2340 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06020011 | 23.5 | 78.5 | 11 | 4.6 | 6345 | 967 | 0.63 | 0.091284 |  | 1.437 |  | 2988 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06020015 | 23.5 | 78.5 | 15 | 6.6 | 8126 | 1238 | 0.81 | 0.071396 |  | 1.361 |  | 3732 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06020016 | 23.5 | 78.5 | 16 | 6.6 | 8761 | 1335 | 0.88 | 0.22873 |  | 1.468 |  | 4168 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06020020 | 23.5 | 78.5 | 20 | 8.6 | 11357 | 1731 | 1.14 | 0.1047 |  | 1.361 |  | 5216 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06020021 | 23.5 | 78.5 | 21 | 8.6 | 12016 | 1831 | 1.2 | 0.17326 |  | 1.493 |  | 5764 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06022010 | 23.5 | 86.5 | 10 | 4.6 | 5577 | 773 | 0.56 | 0.043289 |  | 1.376 |  | 2574 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06022011 | 23.5 | 86.5 | 11 | 4.6 | 6980 | 967 | 0.7 | 0.11773 |  | 1.437 |  | 3287 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06022015 | 23.5 | 86.5 | 15 | 6.6 | 8938 | 1238 | 0.89 | 0.088138 |  | 1.361 |  | 4105 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06022016 | 23.5 | 86.5 | 16 | 6.6 | 9637 | 1335 | 0.96 | 0.27675 |  | 1.468 |  | 4585 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06022020 | 23.5 | 86.5 | 20 | 8.6 | 12494 | 1731 | 1.25 | 0.128 |  | 1.361 |  | 5738 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06022021 | 23.5 | 86.5 | 21 | 8.6 | 13216 | 1831 | 1.32 | 0.21426 |  | 1.493 |  | 6340 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06024010 | 23.5 | 94.5 | 10 | 4.6 | 6084 | 773 | 0.61 | 0.05342 |  | 1.376 |  | 2808 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06024011 | 23.5 | 94.5 | 11 | 4.6 | 7615 | 967 | 0.76 | 0.14488 |  | 1.437 |  | 3586 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06024015 | 23.5 | 94.5 | 15 | 6.6 | 9751 | 1238 | 0.98 | 0.10906 |  | 1.361 |  | 4478 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06024016 | 23.5 | 94.5 | 16 | 6.6 | 10514 | 1335 | 1.05 | 0.33615 |  | 1.468 |  | 5002 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06024020 | 23.5 | 94.5 | 20 | 8.6 | 13629 | 1731 | 1.36 | 0.15396 |  | 1.361 |  | 6259 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06024021 | 23.5 | 94.5 | 21 | 8.6 | 14419 | 1831 | 1.44 | 0.26033 |  | 1.493 |  | 6917 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06026010 | 23.5 | 102.5 | 10 | 4.6 | 6591 | 773 | 0.66 | 0.064887 |  | 1.376 |  | 3042 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06026011 | 23.5 | 102.5 | 11 | 4.6 | 8248 | 967 | 0.82 | 0.17558 |  | 1.437 |  | 3884 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06026015 | 23.5 | 102.5 | 15 | 6.6 | 10565 | 1239 | 1.06 | 0.13021 |  | 1.361 |  | 4852 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06026016 | 23.5 | 102.5 | 16 | 6.6 | 11388 | 1335 | 1.14 | 0.40209 |  | 1.468 |  | 5418 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06026020 | 23.5 | 102.5 | 20 | 8.6 | 14765 | 1731 | 1.48 | 0.18507 |  | 1.361 |  | 6781 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06026021 | 23.5 | 102.5 | 21 | 8.6 | 15620 | 1831 | 1.56 | 0.31163 |  | 1.493 |  | 7493 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06028010 | 23.5 | 110 | 10 | 4.6 | 7098 | 773 | 0.71 | 0.077752 |  | 1.376 |  | 3276 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06028011 | 23.5 | 110 | 11 | 4.6 | 8883 | 967 | 0.89 | 0.21441 |  | 1.437 |  | 4183 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06028015 | 23.5 | 110 | 15 | 6.6 | 11377 | 1238 | 1.14 | 0.15357 |  | 1.361 |  | 5225 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06028016 | 23.5 | 110 | 16 | 6.6 | 12264 | 1335 | 1.23 | 0.47473 |  | 1.468 |  | 5835 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06028020 | 23.5 | 110 | 20 | 8.6 | 15900 | 1731 | 1.59 | 0.21678 |  | 1.361 |  | 7302 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06028021 | 23.5 | 110 | 21 | 8.6 | 16823 | 1831 | 1.68 | 0.36834 |  | 1.493 |  | 8070 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.06030010 | 23.5 | 118 | 10 | 4.6 | 7605 | 773 | 0.76 | 0.092077 |  | 1.376 |  | 3510 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.06030011 | 23.5 | 118 | 11 | 4.6 | 9518 | 967 | 0.95 | 0.25321 |  | 1.437 |  | 4482 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.06030015 | 23.5 | 118 | 15 | 6.6 | 12189 | 1238 | 1.22 | 0.17919 |  | 1.361 |  | 5598 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.06030016 | 23.5 | 118 | 16 | 6.6 | 13141 | 1335 | 1.31 | 0.54617 |  | 1.468 |  | 6252 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.06030020 | 23.5 | 118 | 20 | 8.6 | 17036 | 1731 | 1.7 | 0.25138 |  | 1.361 |  | 7824 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.06030021 | 23.5 | 118 | 21 | 8.6 | 18024 | 1831 | 1.8 | 0.43063 |  | 1.493 |  | 8646 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07004010 | 27.5 | 15.5 | 10 | 4.6 | 1085 | 827 | 0.11 | 0.00092626 |  | 1.366 |  | 499 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07004011 | 27.5 | 15.5 | 11 | 4.6 | 1351 | 1029 | 0.14 | 0.002435 |  | 1.436 |  | 636 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07004015 | 27.5 | 15.5 | 15 | 6.6 | 1724 | 1314 | 0.17 | 0.0024409 |  | 1.35 |  | 789 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07004016 | 27.5 | 15.5 | 16 | 6.6 | 1898 | 1446 | 0.19 | 0.0089402 |  | 1.472 |  | 904 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07004020 | 27.5 | 15.5 | 20 | 8.6 | 2407 | 1834 | 0.24 | 0.0038677 |  | 1.349 |  | 1101 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07004021 | 27.5 | 15.5 | 21 | 8.6 | 2643 | 2014 | 0.26 | 0.0063422 |  | 1.501 |  | 1271 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07005010 | 27.5 | 19.5 | 10 | 4.6 | 1356 | 827 | 0.14 | 0.0015874 |  | 1.366 |  | 624 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07005011 | 27.5 | 19.5 | 11 | 4.6 | 1689 | 1030 | 0.17 | 0.0038442 |  | 1.436 |  | 795 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07005015 | 27.5 | 19.5 | 15 | 6.6 | 2155 | 1314 | 0.22 | 0.0041816 |  | 1.35 |  | 986 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07005016 | 27.5 | 19.5 | 16 | 6.6 | 2372 | 1446 | 0.24 | 0.014487 |  | 1.472 |  | 1130 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07005020 | 27.5 | 19.5 | 20 | 8.6 | 3010 | 1835 | 0.3 | 0.0061434 |  | 1.349 |  | 1377 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07005021 | 27.5 | 19.5 | 21 | 8.6 | 3304 | 2014 | 0.33 | 0.01045 |  | 1.501 |  | 1589 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07006010 | 27.5 | 23.5 | 10 | 4.6 | 1628 | 827 | 0.16 | 0.0021885 |  | 1.366 |  | 749 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07006011 | 27.5 | 23.5 | 11 | 4.6 | 2026 | 1029 | 0.2 | 0.0056486 |  | 1.436 |  | 954 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07006015 | 27.5 | 23.5 | 15 | 6.6 | 2585 | 1313 | 0.26 | 0.0059686 |  | 1.35 |  | 1183 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07006016 | 27.5 | 23.5 | 16 | 6.6 | 2846 | 1446 | 0.28 | 0.020015 |  | 1.472 |  | 1356 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07006020 | 27.5 | 23.5 | 20 | 8.6 | 3611 | 1834 | 0.36 | 0.0089801 |  | 1.349 |  | 1652 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07006021 | 27.5 | 23.5 | 21 | 8.6 | 3963 | 2013 | 0.4 | 0.015669 |  | 1.501 |  | 1906 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07007010 | 27.5 | 27.5 | 10 | 4.6 | 1900 | 827 | 0.19 | 0.0032262 |  | 1.366 |  | 874 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07007011 | 27.5 | 27.5 | 11 | 4.6 | 2364 | 1029 | 0.24 | 0.0085471 |  | 1.436 |  | 1113 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07007015 | 27.5 | 27.5 | 15 | 6.6 | 3016 | 1313 | 0.3 | 0.0081073 |  | 1.35 |  | 1380 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07007016 | 27.5 | 27.5 | 16 | 6.6 | 3321 | 1446 | 0.33 | 0.028168 |  | 1.472 |  | 1582 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07007020 | 27.5 | 27.5 | 20 | 8.6 | 4213 | 1834 | 0.42 | 0.012394 |  | 1.349 |  | 1927 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07007021 | 27.5 | 27.5 | 21 | 8.6 | 4624 | 2013 | 0.46 | 0.021132 |  | 1.501 |  | 2224 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07008010 | 27.5 | 31.5 | 10 | 4.6 | 2169 | 826 | 0.22 | 0.0045043 |  | 1.366 |  | 998 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07008011 | 27.5 | 31.5 | 11 | 4.6 | 2702 | 1029 | 0.27 | 0.011357 |  | 1.436 |  | 1272 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07008015 | 27.5 | 31.5 | 15 | 6.6 | 3448 | 1314 | 0.34 | 0.01061 |  | 1.35 |  | 1578 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07008016 | 27.5 | 31.5 | 16 | 6.6 | 3795 | 1446 | 0.38 | 0.037813 |  | 1.472 |  | 1808 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07008020 | 27.5 | 31.5 | 20 | 8.6 | 4814 | 1834 | 0.48 | 0.0164 |  | 1.349 |  | 2202 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07008021 | 27.5 | 31.5 | 21 | 8.6 | 5285 | 2014 | 0.53 | 0.028549 |  | 1.501 |  | 2542 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07009010 | 27.5 | 35.5 | 10 | 4.6 | 2441 | 827 | 0.24 | 0.0055865 |  | 1.366 |  | 1123 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07009011 | 27.5 | 35.5 | 11 | 4.6 | 3040 | 1030 | 0.3 | 0.01466 |  | 1.436 |  | 1431 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07009015 | 27.5 | 35.5 | 15 | 6.6 | 3879 | 1314 | 0.39 | 0.014192 |  | 1.35 |  | 1775 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07009016 | 27.5 | 35.5 | 16 | 6.6 | 4270 | 1446 | 0.43 | 0.048985 |  | 1.472 |  | 2034 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07009020 | 27.5 | 35.5 | 20 | 8.6 | 5417 | 1835 | 0.54 | 0.021014 |  | 1.349 |  | 2478 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07009021 | 27.5 | 35.5 | 21 | 8.6 | 5944 | 2013 | 0.59 | 0.035993 |  | 1.501 |  | 2859 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07010010 | 27.5 | 39.5 | 10 | 4.6 | 2713 | 827 | 0.27 | 0.0073192 |  | 1.366 |  | 1248 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07010011 | 27.5 | 39.5 | 11 | 4.6 | 3377 | 1029 | 0.34 | 0.019558 |  | 1.436 |  | 1590 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07010015 | 27.5 | 39.5 | 15 | 6.6 | 4310 | 1314 | 0.43 | 0.017544 |  | 1.35 |  | 1972 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07010016 | 27.5 | 39.5 | 16 | 6.6 | 4744 | 1446 | 0.47 | 0.059217 |  | 1.472 |  | 2260 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07010020 | 27.5 | 39.5 | 20 | 8.6 | 6018 | 1834 | 0.6 | 0.02625 |  | 1.349 |  | 2753 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07010021 | 27.5 | 39.5 | 21 | 8.6 | 6605 | 2013 | 0.66 | 0.045749 |  | 1.501 |  | 3177 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07011010 | 27.5 | 43.5 | 10 | 4.6 | 2985 | 827 | 0.3 | 0.0093337 |  | 1.366 |  | 1373 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07011011 | 27.5 | 43.5 | 11 | 4.6 | 3715 | 1029 | 0.37 | 0.024072 |  | 1.436 |  | 1749 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07011015 | 27.5 | 43.5 | 15 | 6.6 | 4740 | 1313 | 0.47 | 0.021296 |  | 1.35 |  | 2169 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07011016 | 27.5 | 43.5 | 16 | 6.6 | 5218 | 1446 | 0.52 | 0.073258 |  | 1.472 |  | 2486 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07011020 | 27.5 | 43.5 | 20 | 8.6 | 6619 | 1834 | 0.66 | 0.032121 |  | 1.349 |  | 3028 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07011021 | 27.5 | 43.5 | 21 | 8.6 | 7266 | 2013 | 0.73 | 0.056806 |  | 1.501 |  | 3495 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07012010 | 27.5 | 47 | 10 | 4.6 | 3256 | 827 | 0.33 | 0.011644 |  | 1.366 |  | 1498 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07012011 | 27.5 | 47 | 11 | 4.6 | 4053 | 1029 | 0.41 | 0.030553 |  | 1.436 |  | 1908 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07012015 | 27.5 | 47 | 15 | 6.6 | 5171 | 1313 | 0.52 | 0.02644 |  | 1.35 |  | 2366 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07012016 | 27.5 | 47 | 16 | 6.6 | 5693 | 1446 | 0.57 | 0.088923 |  | 1.472 |  | 2712 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07012020 | 27.5 | 47 | 20 | 8.6 | 7223 | 1835 | 0.72 | 0.038641 |  | 1.349 |  | 3304 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07012021 | 27.5 | 47 | 21 | 8.6 | 7926 | 2013 | 0.79 | 0.067527 |  | 1.501 |  | 3812 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07014010 | 27.5 | 55 | 10 | 4.6 | 3798 | 827 | 0.38 | 0.016386 |  | 1.366 |  | 1747 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07014011 | 27.5 | 55 | 11 | 4.6 | 4728 | 1029 | 0.47 | 0.042908 |  | 1.436 |  | 2226 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07014015 | 27.5 | 55 | 15 | 6.6 | 6034 | 1314 | 0.6 | 0.036227 |  | 1.35 |  | 2761 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07014016 | 27.5 | 55 | 16 | 6.6 | 6642 | 1446 | 0.66 | 0.12162 |  | 1.472 |  | 3164 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07014020 | 27.5 | 55 | 20 | 8.6 | 8425 | 1834 | 0.84 | 0.053678 |  | 1.349 |  | 3854 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07014021 | 27.5 | 55 | 21 | 8.6 | 9248 | 2013 | 0.92 | 0.094125 |  | 1.501 |  | 4448 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07016010 | 27.5 | 63 | 10 | 4.6 | 4341 | 827 | 0.43 | 0.022142 |  | 1.366 |  | 1997 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07016011 | 27.5 | 63 | 11 | 4.6 | 5404 | 1029 | 0.54 | 0.059971 |  | 1.436 |  | 2544 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07016015 | 27.5 | 63 | 15 | 6.6 | 6895 | 1313 | 0.69 | 0.049158 |  | 1.35 |  | 3155 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07016016 | 27.5 | 63 | 16 | 6.6 | 7590 | 1446 | 0.76 | 0.16421 |  | 1.472 |  | 3616 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07016020 | 27.5 | 63 | 20 | 8.6 | 9630 | 1835 | 0.96 | 0.071463 |  | 1.349 |  | 4405 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07016021 | 27.5 | 63 | 21 | 8.6 | 10568 | 2013 | 1.06 | 0.1281 |  | 1.501 |  | 5083 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07018010 | 27.5 | 71 | 10 | 4.6 | 4882 | 827 | 0.49 | 0.03012 |  | 1.366 |  | 2246 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07018011 | 27.5 | 71 | 11 | 4.6 | 6079 | 1029 | 0.61 | 0.080622 |  | 1.436 |  | 2862 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07018015 | 27.5 | 71 | 15 | 6.6 | 7758 | 1314 | 0.78 | 0.064354 |  | 1.35 |  | 3550 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07018016 | 27.5 | 71 | 16 | 6.6 | 8539 | 1446 | 0.85 | 0.20907 |  | 1.472 |  | 4068 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07018020 | 27.5 | 71 | 20 | 8.6 | 10832 | 1834 | 1.08 | 0.092093 |  | 1.349 |  | 4955 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07018021 | 27.5 | 71 | 21 | 8.6 | 11890 | 2013 | 1.19 | 0.16536 |  | 1.501 |  | 5719 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07020010 | 27.5 | 78.5 | 10 | 4.6 | 5426 | 827 | 0.54 | 0.038288 |  | 1.366 |  | 2496 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07020011 | 27.5 | 78.5 | 11 | 4.6 | 6755 | 1029 | 0.68 | 0.10511 |  | 1.436 |  | 3180 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07020015 | 27.5 | 78.5 | 15 | 6.6 | 8619 | 1314 | 0.86 | 0.080107 |  | 1.35 |  | 3944 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07020016 | 27.5 | 78.5 | 16 | 6.6 | 9488 | 1446 | 0.95 | 0.26543 |  | 1.472 |  | 4520 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07020020 | 27.5 | 78.5 | 20 | 8.6 | 12037 | 1834 | 1.2 | 0.11566 |  | 1.349 |  | 5506 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07020021 | 27.5 | 78.5 | 21 | 8.6 | 13211 | 2013 | 1.32 | 0.20812 |  | 1.501 |  | 6354 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07022010 | 27.5 | 86.5 | 10 | 4.6 | 5969 | 827 | 0.6 | 0.049197 |  | 1.366 |  | 2746 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07022011 | 27.5 | 86.5 | 11 | 4.6 | 7430 | 1029 | 0.74 | 0.13042 |  | 1.436 |  | 3498 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07022015 | 27.5 | 86.5 | 15 | 6.6 | 9480 | 1313 | 0.95 | 0.099885 |  | 1.35 |  | 4338 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07022016 | 27.5 | 86.5 | 16 | 6.6 | 10437 | 1446 | 1.04 | 0.32325 |  | 1.472 |  | 4972 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07022020 | 27.5 | 86.5 | 20 | 8.6 | 13241 | 1834 | 1.32 | 0.14225 |  | 1.349 |  | 6057 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07022021 | 27.5 | 86.5 | 21 | 8.6 | 14531 | 2013 | 1.45 | 0.25658 |  | 1.501 |  | 6989 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07024010 | 27.5 | 94.5 | 10 | 4.6 | 6511 | 827 | 0.65 | 0.06008 |  | 1.366 |  | 2995 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07024011 | 27.5 | 94.5 | 11 | 4.6 | 8106 | 1029 | 0.81 | 0.16287 |  | 1.436 |  | 3816 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07024015 | 27.5 | 94.5 | 15 | 6.6 | 10343 | 1314 | 1.03 | 0.11996 |  | 1.35 |  | 4733 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07024016 | 27.5 | 94.5 | 16 | 6.6 | 11386 | 1446 | 1.14 | 0.39421 |  | 1.472 |  | 5424 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07024020 | 27.5 | 94.5 | 20 | 8.6 | 14443 | 1834 | 1.44 | 0.17196 |  | 1.349 |  | 6607 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07024021 | 27.5 | 94.5 | 21 | 8.6 | 15853 | 2013 | 1.59 | 0.31472 |  | 1.501 |  | 7625 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07026010 | 27.5 | 102.5 | 10 | 4.6 | 7054 | 827 | 0.71 | 0.074249 |  | 1.366 |  | 3245 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07026011 | 27.5 | 102.5 | 11 | 4.6 | 8781 | 1029 | 0.88 | 0.19985 |  | 1.436 |  | 4134 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07026015 | 27.5 | 102.5 | 15 | 6.6 | 11204 | 1313 | 1.12 | 0.14465 |  | 1.35 |  | 5127 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07026016 | 27.5 | 102.5 | 16 | 6.6 | 12334 | 1446 | 1.23 | 0.46574 |  | 1.472 |  | 5876 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07026020 | 27.5 | 102.5 | 20 | 8.6 | 15648 | 1834 | 1.56 | 0.20487 |  | 1.349 |  | 7158 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07026021 | 27.5 | 102.5 | 21 | 8.6 | 17173 | 2013 | 1.72 | 0.37556 |  | 1.501 |  | 8260 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07028010 | 27.5 | 110 | 10 | 4.6 | 7595 | 827 | 0.76 | 0.088135 |  | 1.366 |  | 3494 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07028011 | 27.5 | 110 | 11 | 4.6 | 9457 | 1029 | 0.95 | 0.2416 |  | 1.436 |  | 4452 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07028015 | 27.5 | 110 | 15 | 6.6 | 12068 | 1314 | 1.21 | 0.17204 |  | 1.35 |  | 5522 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07028016 | 27.5 | 110 | 16 | 6.6 | 13283 | 1446 | 1.33 | 0.55208 |  | 1.472 |  | 6328 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07028020 | 27.5 | 110 | 20 | 8.6 | 16850 | 1834 | 1.69 | 0.24384 |  | 1.349 |  | 7708 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07028021 | 27.5 | 110 | 21 | 8.6 | 18496 | 2013 | 1.85 | 0.4427 |  | 1.501 |  | 8896 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.07030010 | 27.5 | 118 | 10 | 4.6 | 8139 | 827 | 0.81 | 0.10352 |  | 1.366 |  | 3744 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.07030011 | 27.5 | 118 | 11 | 4.6 | 10132 | 1029 | 1.01 | 0.28318 |  | 1.436 |  | 4770 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.07030015 | 27.5 | 118 | 15 | 6.6 | 12929 | 1314 | 1.29 | 0.19927 |  | 1.35 |  | 5916 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.07030016 | 27.5 | 118 | 16 | 6.6 | 14232 | 1446 | 1.42 | 0.63805 |  | 1.472 |  | 6780 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.07030020 | 27.5 | 118 | 20 | 8.6 | 18055 | 1834 | 1.81 | 0.28363 |  | 1.349 |  | 8259 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.07030021 | 27.5 | 118 | 21 | 8.6 | 19816 | 2013 | 1.98 | 0.51632 |  | 1.501 |  | 9531 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09004010 | 35.5 | 15.5 | 10 | 4.6 | 1198 | 913 | 0.12 | 0.0010975 |  | 1.348 |  | 548 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09004011 | 35.5 | 15.5 | 11 | 4.6 | 1494 | 1138 | 0.15 | 0.0027841 |  | 1.434 |  | 703 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09004015 | 35.5 | 15.5 | 15 | 6.6 | 1868 | 1423 | 0.19 | 0.0030418 |  | 1.326 |  | 848 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09004016 | 35.5 | 15.5 | 16 | 6.6 | 2173 | 1656 | 0.22 | 0.011962 |  | 1.48 |  | 1038 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09004020 | 35.5 | 15.5 | 20 | 8.6 | 2606 | 1986 | 0.26 | 0.0045338 |  | 1.326 |  | 1183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09004021 | 35.5 | 15.5 | 21 | 8.6 | 3118 | 2376 | 0.31 | 0.0089836 |  | 1.518 |  | 1508 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09005010 | 35.5 | 19.5 | 10 | 4.6 | 1498 | 913 | 0.15 | 0.0018145 |  | 1.348 |  | 685 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09005011 | 35.5 | 19.5 | 11 | 4.6 | 1868 | 1139 | 0.19 | 0.0047639 |  | 1.434 |  | 879 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09005015 | 35.5 | 19.5 | 15 | 6.6 | 2335 | 1423 | 0.23 | 0.0045649 |  | 1.326 |  | 1060 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09005016 | 35.5 | 19.5 | 16 | 6.6 | 2717 | 1656 | 0.27 | 0.018297 |  | 1.48 |  | 1298 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09005020 | 35.5 | 19.5 | 20 | 8.6 | 3258 | 1986 | 0.33 | 0.00742 |  | 1.326 |  | 1479 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09005021 | 35.5 | 19.5 | 21 | 8.6 | 3897 | 2376 | 0.39 | 0.014531 |  | 1.518 |  | 1885 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09006010 | 35.5 | 23.5 | 10 | 4.6 | 1795 | 912 | 0.18 | 0.0027464 |  | 1.348 |  | 821 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09006011 | 35.5 | 23.5 | 11 | 4.6 | 2243 | 1139 | 0.22 | 0.0067812 |  | 1.434 |  | 1055 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09006015 | 35.5 | 23.5 | 15 | 6.6 | 2802 | 1423 | 0.28 | 0.0069056 |  | 1.326 |  | 1272 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09006016 | 35.5 | 23.5 | 16 | 6.6 | 3262 | 1657 | 0.33 | 0.027703 |  | 1.48 |  | 1558 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09006020 | 35.5 | 23.5 | 20 | 8.6 | 3908 | 1985 | 0.39 | 0.01052 |  | 1.326 |  | 1774 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09006021 | 35.5 | 23.5 | 21 | 8.6 | 4677 | 2376 | 0.47 | 0.021525 |  | 1.518 |  | 2262 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09007010 | 35.5 | 27.5 | 10 | 4.6 | 2095 | 912 | 0.21 | 0.0039095 |  | 1.348 |  | 958 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09007011 | 35.5 | 27.5 | 11 | 4.6 | 2617 | 1140 | 0.26 | 0.0099578 |  | 1.434 |  | 1231 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09007015 | 35.5 | 27.5 | 15 | 6.6 | 3269 | 1423 | 0.33 | 0.0097754 |  | 1.326 |  | 1484 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09007016 | 35.5 | 27.5 | 16 | 6.6 | 3804 | 1656 | 0.38 | 0.03722 |  | 1.48 |  | 1817 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09007020 | 35.5 | 27.5 | 20 | 8.6 | 4560 | 1986 | 0.46 | 0.014831 |  | 1.326 |  | 2070 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09007021 | 35.5 | 27.5 | 21 | 8.6 | 5456 | 2376 | 0.55 | 0.030018 |  | 1.518 |  | 2639 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09008010 | 35.5 | 31.5 | 10 | 4.6 | 2395 | 912 | 0.24 | 0.0053196 |  | 1.348 |  | 1095 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09008011 | 35.5 | 31.5 | 11 | 4.6 | 2989 | 1139 | 0.3 | 0.013874 |  | 1.434 |  | 1406 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09008015 | 35.5 | 31.5 | 15 | 6.6 | 3736 | 1423 | 0.37 | 0.012522 |  | 1.326 |  | 1696 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09008016 | 35.5 | 31.5 | 16 | 6.6 | 4348 | 1657 | 0.43 | 0.048251 |  | 1.48 |  | 2077 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09008020 | 35.5 | 31.5 | 20 | 8.6 | 5212 | 1986 | 0.52 | 0.019202 |  | 1.326 |  | 2366 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09008021 | 35.5 | 31.5 | 21 | 8.6 | 6236 | 2376 | 0.62 | 0.038823 |  | 1.518 |  | 3016 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09009010 | 35.5 | 35.5 | 10 | 4.6 | 2694 | 912 | 0.27 | 0.0069919 |  | 1.348 |  | 1232 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09009011 | 35.5 | 35.5 | 11 | 4.6 | 3363 | 1139 | 0.34 | 0.018581 |  | 1.434 |  | 1582 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09009015 | 35.5 | 35.5 | 15 | 6.6 | 4203 | 1423 | 0.42 | 0.016404 |  | 1.326 |  | 1908 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09009016 | 35.5 | 35.5 | 16 | 6.6 | 4891 | 1656 | 0.49 | 0.063353 |  | 1.48 |  | 2336 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09009020 | 35.5 | 35.5 | 20 | 8.6 | 5861 | 1985 | 0.59 | 0.025014 |  | 1.326 |  | 2661 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09009021 | 35.5 | 35.5 | 21 | 8.6 | 7015 | 2376 | 0.7 | 0.050287 |  | 1.518 |  | 3393 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09010010 | 35.5 | 39.5 | 10 | 4.6 | 2994 | 913 | 0.3 | 0.0089407 |  | 1.348 |  | 1369 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09010011 | 35.5 | 39.5 | 11 | 4.6 | 3737 | 1139 | 0.37 | 0.022942 |  | 1.434 |  | 1758 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09010015 | 35.5 | 39.5 | 15 | 6.6 | 4670 | 1423 | 0.47 | 0.020868 |  | 1.326 |  | 2120 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09010016 | 35.5 | 39.5 | 16 | 6.6 | 5435 | 1657 | 0.54 | 0.077806 |  | 1.48 |  | 2596 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09010020 | 35.5 | 39.5 | 20 | 8.6 | 6513 | 1985 | 0.65 | 0.03072 |  | 1.326 |  | 2957 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09010021 | 35.5 | 39.5 | 21 | 8.6 | 7794 | 2376 | 0.78 | 0.063392 |  | 1.518 |  | 3770 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09011010 | 35.5 | 43.5 | 10 | 4.6 | 3293 | 912 | 0.33 | 0.01118 |  | 1.348 |  | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09011011 | 35.5 | 43.5 | 11 | 4.6 | 4111 | 1139 | 0.41 | 0.029202 |  | 1.434 |  | 1934 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09011015 | 35.5 | 43.5 | 15 | 6.6 | 5137 | 1423 | 0.51 | 0.024968 |  | 1.326 |  | 2332 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09011016 | 35.5 | 43.5 | 16 | 6.6 | 5979 | 1657 | 0.6 | 0.09703 |  | 1.48 |  | 2856 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09011020 | 35.5 | 43.5 | 20 | 8.6 | 7165 | 1985 | 0.72 | 0.0381 |  | 1.326 |  | 3253 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09011021 | 35.5 | 43.5 | 21 | 8.6 | 8574 | 2376 | 0.86 | 0.078185 |  | 1.518 |  | 4147 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09012010 | 35.5 | 47 | 10 | 4.6 | 3593 | 913 | 0.36 | 0.013724 |  | 1.348 |  | 1643 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09012011 | 35.5 | 47 | 11 | 4.6 | 4485 | 1139 | 0.45 | 0.036386 |  | 1.434 |  | 2110 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09012015 | 35.5 | 47 | 15 | 6.6 | 5604 | 1423 | 0.56 | 0.030537 |  | 1.326 |  | 2544 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09012016 | 35.5 | 47 | 16 | 6.6 | 6521 | 1656 | 0.65 | 0.11505 |  | 1.48 |  | 3115 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09012020 | 35.5 | 47 | 20 | 8.6 | 7815 | 1985 | 0.78 | 0.045201 |  | 1.326 |  | 3548 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09012021 | 35.5 | 47 | 21 | 8.6 | 9353 | 2376 | 0.94 | 0.094709 |  | 1.518 |  | 4524 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09014010 | 35.5 | 55 | 10 | 4.6 | 4192 | 913 | 0.42 | 0.019778 |  | 1.348 |  | 1917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09014011 | 35.5 | 55 | 11 | 4.6 | 5231 | 1139 | 0.52 | 0.051825 |  | 1.434 |  | 2461 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09014015 | 35.5 | 55 | 15 | 6.6 | 6538 | 1423 | 0.65 | 0.042306 |  | 1.326 |  | 2968 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09014016 | 35.5 | 55 | 16 | 6.6 | 7608 | 1656 | 0.76 | 0.16029 |  | 1.48 |  | 3634 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09014020 | 35.5 | 55 | 20 | 8.6 | 9119 | 1985 | 0.91 | 0.062768 |  | 1.326 |  | 4140 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09014021 | 35.5 | 55 | 21 | 8.6 | 10912 | 2376 | 1.09 | 0.13078 |  | 1.518 |  | 5278 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09016010 | 35.5 | 63 | 10 | 4.6 | 4789 | 912 | 0.48 | 0.027207 |  | 1.348 |  | 2190 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09016011 | 35.5 | 63 | 11 | 4.6 | 5979 | 1139 | 0.6 | 0.072958 |  | 1.434 |  | 2813 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09016015 | 35.5 | 63 | 15 | 6.6 | 7472 | 1423 | 0.75 | 0.057755 |  | 1.326 |  | 3392 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09016016 | 35.5 | 63 | 16 | 6.6 | 8697 | 1657 | 0.87 | 0.21382 |  | 1.48 |  | 4154 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09016020 | 35.5 | 63 | 20 | 8.6 | 10421 | 1985 | 1.04 | 0.083536 |  | 1.326 |  | 4731 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09016021 | 35.5 | 63 | 21 | 8.6 | 12471 | 2376 | 1.25 | 0.17623 |  | 1.518 |  | 6032 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09018010 | 35.5 | 71 | 10 | 4.6 | 5388 | 912 | 0.54 | 0.036109 |  | 1.348 |  | 2464 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09018011 | 35.5 | 71 | 11 | 4.6 | 6725 | 1139 | 0.67 | 0.095939 |  | 1.434 |  | 3164 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09018015 | 35.5 | 71 | 15 | 6.6 | 8406 | 1423 | 0.84 | 0.074237 |  | 1.326 |  | 3816 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09018016 | 35.5 | 71 | 16 | 6.6 | 9783 | 1657 | 0.98 | 0.2759 |  | 1.48 |  | 4673 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09018020 | 35.5 | 71 | 20 | 8.6 | 11725 | 1985 | 1.17 | 0.10762 |  | 1.326 |  | 5323 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09018021 | 35.5 | 71 | 21 | 8.6 | 14030 | 2376 | 1.4 | 0.22627 |  | 1.518 |  | 6786 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09020010 | 35.5 | 78.5 | 10 | 4.6 | 5987 | 912 | 0.6 | 0.046581 |  | 1.348 |  | 2738 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09020011 | 35.5 | 78.5 | 11 | 4.6 | 7474 | 1139 | 0.75 | 0.12598 |  | 1.434 |  | 3516 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09020015 | 35.5 | 78.5 | 15 | 6.6 | 9340 | 1423 | 0.93 | 0.093117 |  | 1.326 |  | 4240 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09020016 | 35.5 | 78.5 | 16 | 6.6 | 10870 | 1657 | 1.09 | 0.34681 |  | 1.48 |  | 5192 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09020020 | 35.5 | 78.5 | 20 | 8.6 | 13027 | 1985 | 1.3 | 0.13511 |  | 1.326 |  | 5914 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09020021 | 35.5 | 78.5 | 21 | 8.6 | 15589 | 2376 | 1.56 | 0.28706 |  | 1.518 |  | 7540 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09022010 | 35.5 | 86.5 | 10 | 4.6 | 6587 | 913 | 0.66 | 0.058715 |  | 1.348 |  | 3012 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09022011 | 35.5 | 86.5 | 11 | 4.6 | 8222 | 1139 | 0.82 | 0.15759 |  | 1.434 |  | 3868 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09022015 | 35.5 | 86.5 | 15 | 6.6 | 10274 | 1423 | 1.03 | 0.11665 |  | 1.326 |  | 4664 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09022016 | 35.5 | 86.5 | 16 | 6.6 | 11956 | 1656 | 1.2 | 0.4268 |  | 1.48 |  | 5711 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09022020 | 35.5 | 86.5 | 20 | 8.6 | 14329 | 1985 | 1.43 | 0.16613 |  | 1.326 |  | 6505 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09022021 | 35.5 | 86.5 | 21 | 8.6 | 17148 | 2376 | 1.71 | 0.35221 |  | 1.518 |  | 8294 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09024010 | 35.5 | 94.5 | 10 | 4.6 | 7186 | 913 | 0.72 | 0.072603 |  | 1.348 |  | 3286 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09024011 | 35.5 | 94.5 | 11 | 4.6 | 8968 | 1139 | 0.9 | 0.19769 |  | 1.434 |  | 4219 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09024015 | 35.5 | 94.5 | 15 | 6.6 | 11208 | 1423 | 1.12 | 0.14083 |  | 1.326 |  | 5088 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09024016 | 35.5 | 94.5 | 16 | 6.6 | 13043 | 1656 | 1.3 | 0.50851 |  | 1.48 |  | 6230 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09024020 | 35.5 | 94.5 | 20 | 8.6 | 15633 | 1985 | 1.56 | 0.20078 |  | 1.326 |  | 7097 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09024021 | 35.5 | 94.5 | 21 | 8.6 | 18707 | 2376 | 1.87 | 0.4295 |  | 1.518 |  | 9048 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09026010 | 35.5 | 102.5 | 10 | 4.6 | 7783 | 912 | 0.78 | 0.088332 |  | 1.348 |  | 3559 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09026011 | 35.5 | 102.5 | 11 | 4.6 | 9716 | 1139 | 0.97 | 0.23895 |  | 1.434 |  | 4571 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09026015 | 35.5 | 102.5 | 15 | 6.6 | 12141 | 1423 | 1.21 | 0.16768 |  | 1.326 |  | 5512 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09026016 | 35.5 | 102.5 | 16 | 6.6 | 14132 | 1657 | 1.41 | 0.60667 |  | 1.48 |  | 6750 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09026020 | 35.5 | 102.5 | 20 | 8.6 | 16935 | 1985 | 1.69 | 0.23914 |  | 1.326 |  | 7688 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09026021 | 35.5 | 102.5 | 21 | 8.6 | 20265 | 2376 | 2.03 | 0.51567 |  | 1.518 |  | 9802 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09028010 | 35.5 | 110 | 10 | 4.6 | 8382 | 912 | 0.84 | 0.10599 |  | 1.348 |  | 3833 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09028011 | 35.5 | 110 | 11 | 4.6 | 10462 | 1139 | 1.05 | 0.2902 |  | 1.434 |  | 4922 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09028015 | 35.5 | 110 | 15 | 6.6 | 13075 | 1423 | 1.31 | 0.20018 |  | 1.326 |  | 5936 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09028016 | 35.5 | 110 | 16 | 6.6 | 15218 | 1657 | 1.52 | 0.71463 |  | 1.48 |  | 7269 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09028020 | 35.5 | 110 | 20 | 8.6 | 18239 | 1985 | 1.82 | 0.28132 |  | 1.326 |  | 8280 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09028021 | 35.5 | 110 | 21 | 8.6 | 21824 | 2376 | 2.18 | 0.60568 |  | 1.518 |  | 10556 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142
Horizontal Wall | Tempo Wall | TEMW.09030010 | 35.5 | 118 | 10 | 4.6 | 8981 | 912 | 0.9 | 0.12566 |  | 1.348 |  | 4107 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Tempo Wall | TEMW.09030011 | 35.5 | 118 | 11 | 4.6 | 11210 | 1139 | 1.12 | 0.34209 |  | 1.434 |  | 5274 | [19 empty] | 0.0003969 | 1.7346 | 4 | 0.00057429
Horizontal Wall | Tempo Wall | TEMW.09030015 | 35.5 | 118 | 15 | 6.6 | 14009 | 1423 | 1.4 | 0.23287 |  | 1.326 |  | 6360 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Tempo Wall | TEMW.09030016 | 35.5 | 118 | 16 | 6.6 | 16305 | 1657 | 1.63 | 0.83263 |  | 1.48 |  | 7788 | [19 empty] | 0.0002083 | 1.724 | 4 | 0.0013928
Horizontal Wall | Tempo Wall | TEMW.09030020 | 35.5 | 118 | 20 | 8.6 | 19540 | 1985 | 1.95 | 0.32741 |  | 1.326 |  | 8871 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Tempo Wall | TEMW.09030021 | 35.5 | 118 | 21 | 8.6 | 23383 | 2376 | 2.34 | 0.70996 |  | 1.518 |  | 11310 | [19 empty] | 0.0001276 | 1.7219 | 4 | 0.0005142

## Strada Cont.
Selection Model 2022-10 | [36 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF | [27 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF | [13 empty] | h(mm) | 0 | [12 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF | [13 empty] | cf_h | 1 | [12 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF | [28 empty] | -10
[11 empty] | *Sound pressure with an assumed room damping of 8dB(A) | [26 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º |  |  |  |  | N-Waarde | 75/65/20ºC |  | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  |  |  | 16/18/27ºC
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | BTU/h per foot | Flow in GPM | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | 100% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | k1 | n | t | k2 | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | SalesGroup | JagaSourceCode Stnd
Horizontal Wall | Strada Continua | STCA.03505005 | 14 | 19.5 | 05 | 2.8 | 543 | 331 | 0.05 | 0.00035667 |  | 1.392 | 252 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03505010 | 14 | 19.5 | 10 | 4.8 | 765 | 466 | 0.08 | 0.00053785 |  | 1.41 | 357 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03505015 | 14 | 19.5 | 15 | 6.8 | 1168 | 712 | 0.12 | 0.0012664 |  | 1.408 | 545 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03506005 | 14 | 23.5 | 05 | 2.8 | 651 | 331 | 0.07 | 0.00076306 |  | 1.392 | 302 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03506010 | 14 | 23.5 | 10 | 4.8 | 915 | 465 | 0.09 | 0.0007239 |  | 1.41 | 427 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03506015 | 14 | 23.5 | 15 | 6.8 | 1402 | 712 | 0.14 | 0.0017685 |  | 1.408 | 654 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03507005 | 14 | 27.5 | 05 | 2.8 | 759 | 330 | 0.08 | 0.0010923 |  | 1.392 | 352 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03507010 | 14 | 27.5 | 10 | 4.8 | 1067 | 465 | 0.11 | 0.0011331 |  | 1.41 | 498 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03507015 | 14 | 27.5 | 15 | 6.8 | 1636 | 712 | 0.16 | 0.0023652 |  | 1.408 | 763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03508005 | 14 | 31.5 | 05 | 2.8 | 866 | 330 | 0.09 | 0.0014993 |  | 1.392 | 402 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03508010 | 14 | 31.5 | 10 | 4.8 | 1219 | 464 | 0.12 | 0.0014183 |  | 1.41 | 569 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03508015 | 14 | 31.5 | 15 | 6.8 | 1869 | 712 | 0.19 | 0.0034008 |  | 1.408 | 872 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03509005 | 14 | 35.5 | 05 | 2.8 | 976 | 331 | 0.1 | 0.0019909 |  | 1.392 | 453 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03509010 | 14 | 35.5 | 10 | 4.8 | 1371 | 464 | 0.14 | 0.0020066 |  | 1.41 | 640 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03509015 | 14 | 35.5 | 15 | 6.8 | 2103 | 712 | 0.21 | 0.0042415 |  | 1.408 | 981 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03510005 | 14 | 39.5 | 05 | 2.8 | 1084 | 330 | 0.11 | 0.0025736 |  | 1.392 | 503 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03510010 | 14 | 39.5 | 10 | 4.8 | 1523 | 464 | 0.15 | 0.002405 |  | 1.41 | 711 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03510015 | 14 | 39.5 | 15 | 6.8 | 2337 | 712 | 0.23 | 0.0051886 |  | 1.408 | 1090 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03511005 | 14 | 43.5 | 05 | 2.8 | 1192 | 330 | 0.12 | 0.0032541 |  | 1.392 | 553 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03511010 | 14 | 43.5 | 10 | 4.8 | 1675 | 464 | 0.17 | 0.0031935 |  | 1.41 | 782 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03511015 | 14 | 43.5 | 15 | 6.8 | 2571 | 712 | 0.26 | 0.0067392 |  | 1.408 | 1199 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03512005 | 14 | 47 | 05 | 2.8 | 1302 | 331 | 0.13 | 0.0040387 |  | 1.392 | 604 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03512010 | 14 | 47 | 10 | 4.8 | 1828 | 464 | 0.18 | 0.0037186 |  | 1.41 | 853 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03512015 | 14 | 47 | 15 | 6.8 | 2804 | 712 | 0.28 | 0.0079564 |  | 1.408 | 1308 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03514005 | 14 | 55 | 05 | 2.8 | 1517 | 330 | 0.15 | 0.0059452 |  | 1.392 | 704 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03514010 | 14 | 55 | 10 | 4.8 | 2132 | 464 | 0.21 | 0.0053914 |  | 1.41 | 995 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03514015 | 14 | 55 | 15 | 6.8 | 3272 | 712 | 0.33 | 0.011403 |  | 1.408 | 1526 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03516005 | 14 | 63 | 05 | 2.8 | 1735 | 331 | 0.17 | 0.0083419 |  | 1.392 | 805 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03516010 | 14 | 63 | 10 | 4.8 | 2438 | 464 | 0.24 | 0.0074547 |  | 1.41 | 1138 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03516015 | 14 | 63 | 15 | 6.8 | 3739 | 712 | 0.37 | 0.014787 |  | 1.408 | 1744 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03518005 | 14 | 71 | 05 | 2.8 | 1951 | 330 | 0.2 | 0.012393 |  | 1.392 | 905 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03518010 | 14 | 71 | 10 | 4.8 | 2742 | 464 | 0.27 | 0.0099382 |  | 1.41 | 1280 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03518015 | 14 | 71 | 15 | 6.8 | 4206 | 712 | 0.42 | 0.019575 |  | 1.408 | 1962 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03520005 | 14 | 78.5 | 05 | 2.8 | 2168 | 330 | 0.22 | 0.016114 |  | 1.392 | 1006 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03520010 | 14 | 78.5 | 10 | 4.8 | 3047 | 464 | 0.3 | 0.012871 |  | 1.41 | 1422 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03520015 | 14 | 78.5 | 15 | 6.8 | 4674 | 712 | 0.47 | 0.025145 |  | 1.408 | 2180 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03522005 | 14 | 86.5 | 05 | 2.8 | 2386 | 331 | 0.24 | 0.020479 |  | 1.392 | 1107 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03522010 | 14 | 86.5 | 10 | 4.8 | 3351 | 464 | 0.34 | 0.017202 |  | 1.41 | 1564 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03522015 | 14 | 86.5 | 15 | 6.8 | 5141 | 712 | 0.51 | 0.030384 |  | 1.408 | 2398 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03524005 | 14 | 94.5 | 05 | 2.8 | 2601 | 330 | 0.26 | 0.025532 |  | 1.392 | 1207 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03524010 | 14 | 94.5 | 10 | 4.8 | 3655 | 464 | 0.37 | 0.021239 |  | 1.41 | 1706 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03524015 | 14 | 94.5 | 15 | 6.8 | 5608 | 712 | 0.56 | 0.03748 |  | 1.408 | 2616 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03526005 | 14 | 102.5 | 05 | 2.8 | 2819 | 330 | 0.28 | 0.031315 |  | 1.392 | 1308 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03526010 | 14 | 102.5 | 10 | 4.8 | 3961 | 464 | 0.4 | 0.025812 |  | 1.41 | 1849 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03526015 | 14 | 102.5 | 15 | 6.8 | 6076 | 712 | 0.61 | 0.045451 |  | 1.408 | 2834 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.03528005 | 14 | 110 | 05 | 2.8 | 3035 | 330 | 0.3 | 0.03787 |  | 1.392 | 1408 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continua | STCA.03528010 | 14 | 110 | 10 | 4.8 | 4266 | 464 | 0.43 | 0.030948 |  | 1.41 | 1991 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.03528015 | 14 | 110 | 15 | 6.8 | 6543 | 712 | 0.65 | 0.052778 |  | 1.408 | 3052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05005010 | 19.5 | 19.5 | 10 | 4.8 | 1038 | 633 | 0.1 | 0.00082769 |  | 1.394 | 482 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05005015 | 19.5 | 19.5 | 15 | 6.8 | 1585 | 966 | 0.16 | 0.0022317 |  | 1.39 | 735 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05005020 | 19.5 | 19.5 | 20 | 8.7 | 2373 | 1447 | 0.24 | 0.0039492 |  | 1.384 | 1098 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05006010 | 19.5 | 23.5 | 10 | 4.8 | 1245 | 632 | 0.12 | 0.0012579 |  | 1.394 | 578 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05006015 | 19.5 | 23.5 | 15 | 6.8 | 1902 | 966 | 0.19 | 0.0032213 |  | 1.39 | 882 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05006020 | 19.5 | 23.5 | 20 | 8.7 | 2848 | 1447 | 0.28 | 0.0054651 |  | 1.384 | 1318 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05007010 | 19.5 | 27.5 | 10 | 4.8 | 1452 | 632 | 0.15 | 0.0020507 |  | 1.394 | 674 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05007015 | 19.5 | 27.5 | 15 | 6.8 | 2219 | 966 | 0.22 | 0.0044127 |  | 1.39 | 1029 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05007020 | 19.5 | 27.5 | 20 | 8.7 | 3321 | 1446 | 0.33 | 0.0077023 |  | 1.384 | 1537 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05008010 | 19.5 | 31.5 | 10 | 4.8 | 1658 | 632 | 0.17 | 0.0027532 |  | 1.394 | 770 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05008015 | 19.5 | 31.5 | 15 | 6.8 | 2536 | 966 | 0.25 | 0.0058134 |  | 1.39 | 1176 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05008020 | 19.5 | 31.5 | 20 | 8.7 | 3797 | 1447 | 0.38 | 0.010353 |  | 1.384 | 1757 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05009010 | 19.5 | 35.5 | 10 | 4.8 | 1867 | 632 | 0.19 | 0.0035822 |  | 1.394 | 867 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05009015 | 19.5 | 35.5 | 15 | 6.8 | 2853 | 966 | 0.29 | 0.0079576 |  | 1.39 | 1323 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05009020 | 19.5 | 35.5 | 20 | 8.7 | 4270 | 1446 | 0.43 | 0.013428 |  | 1.384 | 1976 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05010010 | 19.5 | 39.5 | 10 | 4.8 | 2074 | 632 | 0.21 | 0.0045446 |  | 1.394 | 963 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05010015 | 19.5 | 39.5 | 15 | 6.8 | 3170 | 966 | 0.32 | 0.0098637 |  | 1.39 | 1470 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05010020 | 19.5 | 39.5 | 20 | 8.7 | 4745 | 1446 | 0.47 | 0.016253 |  | 1.384 | 2196 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05011010 | 19.5 | 43.5 | 10 | 4.8 | 2281 | 632 | 0.23 | 0.0056475 |  | 1.394 | 1059 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05011015 | 19.5 | 43.5 | 15 | 6.8 | 3487 | 966 | 0.35 | 0.012002 |  | 1.39 | 1617 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05011020 | 19.5 | 43.5 | 20 | 8.7 | 5221 | 1447 | 0.52 | 0.020128 |  | 1.384 | 2416 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05012010 | 19.5 | 47 | 10 | 4.8 | 2490 | 632 | 0.25 | 0.0068976 |  | 1.394 | 1156 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05012015 | 19.5 | 47 | 15 | 6.8 | 3804 | 966 | 0.38 | 0.014379 |  | 1.39 | 1764 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05012020 | 19.5 | 47 | 20 | 8.7 | 5694 | 1446 | 0.57 | 0.024458 |  | 1.384 | 2635 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05014010 | 19.5 | 55 | 10 | 4.8 | 2903 | 632 | 0.29 | 0.0098653 |  | 1.394 | 1348 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05014015 | 19.5 | 55 | 15 | 6.8 | 4438 | 966 | 0.44 | 0.019875 |  | 1.39 | 2058 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05014020 | 19.5 | 55 | 20 | 8.7 | 6643 | 1446 | 0.66 | 0.033517 |  | 1.384 | 3074 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05016010 | 19.5 | 63 | 10 | 4.8 | 3319 | 632 | 0.33 | 0.013499 |  | 1.394 | 1541 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05016015 | 19.5 | 63 | 15 | 6.8 | 5073 | 966 | 0.51 | 0.02743 |  | 1.39 | 2352 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05016020 | 19.5 | 63 | 20 | 8.7 | 7594 | 1447 | 0.76 | 0.045332 |  | 1.384 | 3514 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05018010 | 19.5 | 71 | 10 | 4.8 | 3733 | 632 | 0.37 | 0.017846 |  | 1.394 | 1733 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05018015 | 19.5 | 71 | 15 | 6.8 | 5707 | 966 | 0.57 | 0.035186 |  | 1.39 | 2646 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05018020 | 19.5 | 71 | 20 | 8.7 | 8542 | 1446 | 0.85 | 0.057812 |  | 1.384 | 3953 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05020010 | 19.5 | 78.5 | 10 | 4.8 | 4148 | 632 | 0.41 | 0.022956 |  | 1.394 | 1926 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05020015 | 19.5 | 78.5 | 15 | 6.8 | 6341 | 966 | 0.63 | 0.044072 |  | 1.39 | 2940 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05020020 | 19.5 | 78.5 | 20 | 8.7 | 9491 | 1446 | 0.95 | 0.073505 |  | 1.384 | 4392 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05022010 | 19.5 | 86.5 | 10 | 4.8 | 4564 | 632 | 0.46 | 0.030071 |  | 1.394 | 2119 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05022015 | 19.5 | 86.5 | 15 | 6.8 | 6975 | 966 | 0.7 | 0.055644 |  | 1.39 | 3234 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05022020 | 19.5 | 86.5 | 20 | 8.7 | 10440 | 1446 | 1.04 | 0.089647 |  | 1.384 | 4831 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05024010 | 19.5 | 94.5 | 10 | 4.8 | 4978 | 632 | 0.5 | 0.036997 |  | 1.394 | 2311 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05024015 | 19.5 | 94.5 | 15 | 6.8 | 7609 | 966 | 0.76 | 0.067088 |  | 1.39 | 3528 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05024020 | 19.5 | 94.5 | 20 | 8.7 | 11388 | 1446 | 1.14 | 0.10947 |  | 1.384 | 5270 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05026010 | 19.5 | 102.5 | 10 | 4.8 | 5393 | 632 | 0.54 | 0.044825 |  | 1.394 | 2504 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05026015 | 19.5 | 102.5 | 15 | 6.8 | 8243 | 966 | 0.82 | 0.079798 |  | 1.39 | 3822 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05026020 | 19.5 | 102.5 | 20 | 8.7 | 12339 | 1447 | 1.23 | 0.1295 |  | 1.384 | 5710 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.05028010 | 19.5 | 110 | 10 | 4.8 | 5807 | 632 | 0.58 | 0.053598 |  | 1.394 | 2696 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.05028015 | 19.5 | 110 | 15 | 6.8 | 8877 | 966 | 0.89 | 0.095853 |  | 1.39 | 4116 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.05028020 | 19.5 | 110 | 20 | 8.7 | 13288 | 1446 | 1.33 | 0.15368 |  | 1.384 | 6149 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06505010 | 25.5 | 19.5 | 10 | 4.8 | 1162 | 708 | 0.12 | 0.0011777 |  | 1.385 | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06505015 | 25.5 | 19.5 | 15 | 6.8 | 1880 | 1146 | 0.19 | 0.0031316 |  | 1.373 | 867 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06505020 | 25.5 | 19.5 | 20 | 8.7 | 2631 | 1604 | 0.26 | 0.0046274 |  | 1.373 | 1213 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06506010 | 25.5 | 23.5 | 10 | 4.8 | 1396 | 709 | 0.14 | 0.0016922 |  | 1.385 | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06506015 | 25.5 | 23.5 | 15 | 6.8 | 2256 | 1146 | 0.23 | 0.0046896 |  | 1.373 | 1040 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06506020 | 25.5 | 23.5 | 20 | 8.7 | 3156 | 1603 | 0.32 | 0.007115 |  | 1.373 | 1455 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06507010 | 25.5 | 27.5 | 10 | 4.8 | 1627 | 708 | 0.16 | 0.0023206 |  | 1.385 | 753 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06507015 | 25.5 | 27.5 | 15 | 6.8 | 2633 | 1146 | 0.26 | 0.0061227 |  | 1.373 | 1214 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06507020 | 25.5 | 27.5 | 20 | 8.7 | 3683 | 1604 | 0.37 | 0.0096517 |  | 1.373 | 1698 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06508010 | 25.5 | 31.5 | 10 | 4.8 | 1860 | 709 | 0.19 | 0.0034042 |  | 1.385 | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06508015 | 25.5 | 31.5 | 15 | 6.8 | 3008 | 1146 | 0.3 | 0.0083046 |  | 1.373 | 1387 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06508020 | 25.5 | 31.5 | 20 | 8.7 | 4208 | 1603 | 0.42 | 0.012608 |  | 1.373 | 1940 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06509010 | 25.5 | 35.5 | 10 | 4.8 | 2091 | 708 | 0.21 | 0.0043329 |  | 1.385 | 968 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06509015 | 25.5 | 35.5 | 15 | 6.8 | 3386 | 1147 | 0.34 | 0.010855 |  | 1.373 | 1561 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06509020 | 25.5 | 35.5 | 20 | 8.7 | 4735 | 1604 | 0.47 | 0.015994 |  | 1.373 | 2183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06510010 | 25.5 | 39.5 | 10 | 4.8 | 2324 | 708 | 0.23 | 0.0053996 |  | 1.385 | 1076 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06510015 | 25.5 | 39.5 | 15 | 6.8 | 3761 | 1146 | 0.38 | 0.013786 |  | 1.373 | 1734 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06510020 | 25.5 | 39.5 | 20 | 8.7 | 5259 | 1603 | 0.53 | 0.020575 |  | 1.373 | 2425 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06511010 | 25.5 | 43.5 | 10 | 4.8 | 2558 | 709 | 0.26 | 0.0071199 |  | 1.385 | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06511015 | 25.5 | 43.5 | 15 | 6.8 | 4136 | 1146 | 0.41 | 0.016325 |  | 1.373 | 1907 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06511020 | 25.5 | 43.5 | 20 | 8.7 | 5786 | 1603 | 0.58 | 0.024932 |  | 1.373 | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06512010 | 25.5 | 47 | 10 | 4.8 | 2789 | 708 | 0.28 | 0.0085399 |  | 1.385 | 1291 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06512015 | 25.5 | 47 | 15 | 6.8 | 4513 | 1146 | 0.45 | 0.019964 |  | 1.373 | 2081 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06512020 | 25.5 | 47 | 20 | 8.7 | 6311 | 1603 | 0.63 | 0.02975 |  | 1.373 | 2910 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06514010 | 25.5 | 55 | 10 | 4.8 | 3253 | 708 | 0.33 | 0.012571 |  | 1.385 | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06514015 | 25.5 | 55 | 15 | 6.8 | 5266 | 1146 | 0.53 | 0.028489 |  | 1.373 | 2428 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06514020 | 25.5 | 55 | 20 | 8.7 | 7363 | 1603 | 0.74 | 0.041905 |  | 1.373 | 3395 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06516010 | 25.5 | 63 | 10 | 4.8 | 3720 | 709 | 0.37 | 0.016715 |  | 1.385 | 1722 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06516015 | 25.5 | 63 | 15 | 6.8 | 6016 | 1146 | 0.6 | 0.03753 |  | 1.373 | 2774 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06516020 | 25.5 | 63 | 20 | 8.7 | 8415 | 1603 | 0.84 | 0.055088 |  | 1.373 | 3880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06518010 | 25.5 | 71 | 10 | 4.8 | 4184 | 708 | 0.42 | 0.022597 |  | 1.385 | 1937 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06518015 | 25.5 | 71 | 15 | 6.8 | 6769 | 1146 | 0.68 | 0.049408 |  | 1.373 | 3121 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06518020 | 25.5 | 71 | 20 | 8.7 | 9467 | 1603 | 0.95 | 0.071762 |  | 1.373 | 4365 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06520010 | 25.5 | 78.5 | 10 | 4.8 | 4649 | 709 | 0.46 | 0.028422 |  | 1.385 | 2152 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06520015 | 25.5 | 78.5 | 15 | 6.8 | 7521 | 1146 | 0.75 | 0.061584 |  | 1.373 | 3468 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06520020 | 25.5 | 78.5 | 20 | 8.7 | 10519 | 1603 | 1.05 | 0.089252 |  | 1.373 | 4850 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06522010 | 25.5 | 86.5 | 10 | 4.8 | 5113 | 708 | 0.51 | 0.036401 |  | 1.385 | 2367 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06522015 | 25.5 | 86.5 | 15 | 6.8 | 8274 | 1146 | 0.83 | 0.077102 |  | 1.373 | 3815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06522020 | 25.5 | 86.5 | 20 | 8.7 | 11571 | 1603 | 1.16 | 0.11075 |  | 1.373 | 5335 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06524010 | 25.5 | 94.5 | 10 | 4.8 | 5578 | 708 | 0.56 | 0.045609 |  | 1.385 | 2582 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06524015 | 25.5 | 94.5 | 15 | 6.8 | 9027 | 1146 | 0.9 | 0.092669 |  | 1.373 | 4162 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06524020 | 25.5 | 94.5 | 20 | 8.7 | 12623 | 1603 | 1.26 | 0.13282 |  | 1.373 | 5820 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06526010 | 25.5 | 102.5 | 10 | 4.8 | 6044 | 709 | 0.6 | 0.054428 |  | 1.385 | 2798 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06526015 | 25.5 | 102.5 | 15 | 6.8 | 9777 | 1146 | 0.98 | 0.1121 |  | 1.373 | 4508 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06526020 | 25.5 | 102.5 | 20 | 8.7 | 13674 | 1603 | 1.37 | 0.15943 |  | 1.373 | 6305 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continua | STCA.06528010 | 25.5 | 110 | 10 | 4.8 | 6509 | 709 | 0.65 | 0.066091 |  | 1.385 | 3013 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continua | STCA.06528015 | 25.5 | 110 | 15 | 6.8 | 10530 | 1146 | 1.05 | 0.1313 |  | 1.373 | 4855 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continua | STCA.06528020 | 25.5 | 110 | 20 | 8.7 | 14726 | 1603 | 1.47 | 0.18636 |  | 1.373 | 6790 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.02005005 | 8 | 19.5 | 05 | 2.8 | 488 | 297 | 0.05 | 0.00035667 |  | 1.399 | 227 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02005010 | 8 | 19.5 | 10 | 4.8 | 702 | 428 | 0.07 | 0.00041569 |  | 1.413 | 328 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02005015 | 8 | 19.5 | 15 | 6.8 | 1168 | 712 | 0.12 | 0.0012664 |  | 1.408 | 545 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02006005 | 8 | 23.5 | 05 | 2.8 | 585 | 297 | 0.06 | 0.00057017 |  | 1.399 | 272 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02006010 | 8 | 23.5 | 10 | 4.8 | 841 | 427 | 0.08 | 0.00057754 |  | 1.413 | 393 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02006015 | 8 | 23.5 | 15 | 6.8 | 1402 | 712 | 0.14 | 0.0017685 |  | 1.408 | 654 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02007005 | 8 | 27.5 | 05 | 2.8 | 684 | 298 | 0.07 | 0.00084964 |  | 1.399 | 318 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02007010 | 8 | 27.5 | 10 | 4.8 | 982 | 428 | 0.1 | 0.0009446 |  | 1.413 | 459 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02007015 | 8 | 27.5 | 15 | 6.8 | 1636 | 712 | 0.16 | 0.0023652 |  | 1.408 | 763 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02008005 | 8 | 31.5 | 05 | 2.8 | 781 | 298 | 0.08 | 0.0012023 |  | 1.399 | 363 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02008010 | 8 | 31.5 | 10 | 4.8 | 1122 | 427 | 0.11 | 0.0012021 |  | 1.413 | 524 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02008015 | 8 | 31.5 | 15 | 6.8 | 1869 | 712 | 0.19 | 0.0034008 |  | 1.408 | 872 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02009005 | 8 | 35.5 | 05 | 2.8 | 879 | 298 | 0.09 | 0.0016351 |  | 1.399 | 409 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02009010 | 8 | 35.5 | 10 | 4.8 | 1263 | 428 | 0.13 | 0.0017437 |  | 1.413 | 590 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02009015 | 8 | 35.5 | 15 | 6.8 | 2103 | 712 | 0.21 | 0.0042415 |  | 1.408 | 981 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02010005 | 8 | 39.5 | 05 | 2.8 | 976 | 297 | 0.1 | 0.0021548 |  | 1.399 | 454 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02010010 | 8 | 39.5 | 10 | 4.8 | 1402 | 427 | 0.14 | 0.0021113 |  | 1.413 | 655 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02010015 | 8 | 39.5 | 15 | 6.8 | 2337 | 712 | 0.23 | 0.0051886 |  | 1.408 | 1090 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02011005 | 8 | 43.5 | 05 | 2.8 | 1073 | 297 | 0.11 | 0.002768 |  | 1.399 | 499 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02011010 | 8 | 43.5 | 10 | 4.8 | 1543 | 428 | 0.15 | 0.0025231 |  | 1.413 | 721 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02011015 | 8 | 43.5 | 15 | 6.8 | 2571 | 712 | 0.26 | 0.0067392 |  | 1.408 | 1199 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02012005 | 8 | 47 | 05 | 2.8 | 1172 | 298 | 0.12 | 0.0034813 |  | 1.399 | 545 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02012010 | 8 | 47 | 10 | 4.8 | 1682 | 427 | 0.17 | 0.0033402 |  | 1.413 | 786 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02012015 | 8 | 47 | 15 | 6.8 | 2804 | 712 | 0.28 | 0.0079564 |  | 1.408 | 1308 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02014005 | 8 | 55 | 05 | 2.8 | 1368 | 298 | 0.14 | 0.005233 |  | 1.399 | 636 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02014010 | 8 | 55 | 10 | 4.8 | 1963 | 427 | 0.2 | 0.0049216 |  | 1.413 | 917 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02014015 | 8 | 55 | 15 | 6.8 | 3272 | 712 | 0.33 | 0.011403 |  | 1.408 | 1526 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02016005 | 8 | 63 | 05 | 2.8 | 1561 | 297 | 0.16 | 0.0074594 |  | 1.399 | 726 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02016010 | 8 | 63 | 10 | 4.8 | 2243 | 427 | 0.22 | 0.0063403 |  | 1.413 | 1048 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02016015 | 8 | 63 | 15 | 6.8 | 3739 | 712 | 0.37 | 0.014787 |  | 1.408 | 1744 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02018005 | 8 | 71 | 05 | 2.8 | 1757 | 298 | 0.18 | 0.010208 |  | 1.399 | 817 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02018010 | 8 | 71 | 10 | 4.8 | 2524 | 427 | 0.25 | 0.0086163 |  | 1.413 | 1179 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02018015 | 8 | 71 | 15 | 6.8 | 4206 | 712 | 0.42 | 0.019575 |  | 1.408 | 1962 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02020005 | 8 | 78.5 | 05 | 2.8 | 1952 | 297 | 0.2 | 0.013526 |  | 1.399 | 908 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02020010 | 8 | 78.5 | 10 | 4.8 | 2804 | 427 | 0.28 | 0.011329 |  | 1.413 | 1310 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02020015 | 8 | 78.5 | 15 | 6.8 | 4674 | 712 | 0.47 | 0.025145 |  | 1.408 | 2180 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02022005 | 8 | 86.5 | 05 | 2.8 | 2148 | 298 | 0.21 | 0.016032 |  | 1.399 | 999 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02022010 | 8 | 86.5 | 10 | 4.8 | 3084 | 427 | 0.31 | 0.014508 |  | 1.413 | 1441 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02022015 | 8 | 86.5 | 15 | 6.8 | 5141 | 712 | 0.51 | 0.030384 |  | 1.408 | 2398 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02024005 | 8 | 94.5 | 05 | 2.8 | 2344 | 298 | 0.23 | 0.020397 |  | 1.399 | 1090 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02024010 | 8 | 94.5 | 10 | 4.8 | 3365 | 427 | 0.34 | 0.018179 |  | 1.413 | 1572 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02024015 | 8 | 94.5 | 15 | 6.8 | 5608 | 712 | 0.56 | 0.03748 |  | 1.408 | 2616 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.02026005 | 8 | 102.5 | 05 | 2.8 | 2537 | 297 | 0.25 | 0.025452 |  | 1.399 | 1180 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02026010 | 8 | 102.5 | 10 | 4.8 | 3645 | 427 | 0.36 | 0.021273 |  | 1.413 | 1703 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02026010 | 8 | 102.5 | 10 | 4.8 | 3645 | 427 | 0.36 | 0.021273 |  | 1.413 | 1703 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02028005 | 8 | 110 | 05 | 2.8 | 2733 | 298 | 0.27 | 0.031239 |  | 1.399 | 1271 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.02028010 | 8 | 110 | 10 | 4.8 | 3925 | 427 | 0.39 | 0.025879 |  | 1.413 | 1834 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.02028015 | 8 | 110 | 15 | 6.8 | 6543 | 712 | 0.65 | 0.052778 |  | 1.408 | 3052 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03505005 | 14 | 19.5 | 05 | 2.8 | 543 | 331 | 0.05 | 0.00035667 |  | 1.392 | 252 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03505010 | 14 | 19.5 | 10 | 4.8 | 965 | 588 | 0.1 | 0.00082769 |  | 1.399 | 449 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03505015 | 14 | 19.5 | 15 | 6.8 | 1585 | 966 | 0.16 | 0.0022317 |  | 1.39 | 735 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03506005 | 14 | 23.5 | 05 | 2.8 | 651 | 331 | 0.07 | 0.00076306 |  | 1.392 | 302 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03506010 | 14 | 23.5 | 10 | 4.8 | 1159 | 589 | 0.12 | 0.0012579 |  | 1.399 | 539 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03506015 | 14 | 23.5 | 15 | 6.8 | 1902 | 966 | 0.19 | 0.0032213 |  | 1.39 | 882 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03507005 | 14 | 27.5 | 05 | 2.8 | 759 | 330 | 0.08 | 0.0010923 |  | 1.392 | 352 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03507010 | 14 | 27.5 | 10 | 4.8 | 1353 | 589 | 0.14 | 0.001797 |  | 1.399 | 629 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03507015 | 14 | 27.5 | 15 | 6.8 | 2219 | 966 | 0.22 | 0.0044127 |  | 1.39 | 1029 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03508005 | 14 | 31.5 | 05 | 2.8 | 866 | 330 | 0.09 | 0.0014993 |  | 1.392 | 402 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03508010 | 14 | 31.5 | 10 | 4.8 | 1544 | 588 | 0.15 | 0.0021688 |  | 1.399 | 718 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03508015 | 14 | 31.5 | 15 | 6.8 | 2536 | 966 | 0.25 | 0.0058134 |  | 1.39 | 1176 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03509005 | 14 | 35.5 | 05 | 2.8 | 976 | 331 | 0.1 | 0.0019909 |  | 1.392 | 453 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03509010 | 14 | 35.5 | 10 | 4.8 | 1737 | 588 | 0.17 | 0.0029 |  | 1.399 | 808 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03509015 | 14 | 35.5 | 15 | 6.8 | 2853 | 966 | 0.29 | 0.0079576 |  | 1.39 | 1323 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03510005 | 14 | 39.5 | 05 | 2.8 | 1084 | 330 | 0.11 | 0.0025736 |  | 1.392 | 503 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03510010 | 14 | 39.5 | 10 | 4.8 | 1931 | 589 | 0.19 | 0.0037601 |  | 1.399 | 898 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03510015 | 14 | 39.5 | 15 | 6.8 | 3170 | 966 | 0.32 | 0.0098637 |  | 1.39 | 1470 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03511005 | 14 | 43.5 | 05 | 2.8 | 1192 | 330 | 0.12 | 0.0032541 |  | 1.392 | 553 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03511010 | 14 | 43.5 | 10 | 4.8 | 2124 | 589 | 0.21 | 0.0047563 |  | 1.399 | 988 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03511015 | 14 | 43.5 | 15 | 6.8 | 3487 | 966 | 0.35 | 0.012002 |  | 1.39 | 1617 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03512005 | 14 | 47 | 05 | 2.8 | 1302 | 331 | 0.13 | 0.0040387 |  | 1.392 | 604 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03512010 | 14 | 47 | 10 | 4.8 | 2318 | 589 | 0.23 | 0.0058954 |  | 1.399 | 1078 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03512015 | 14 | 47 | 15 | 6.8 | 3804 | 966 | 0.38 | 0.014379 |  | 1.39 | 1764 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03514005 | 14 | 55 | 05 | 2.8 | 1517 | 330 | 0.15 | 0.0059452 |  | 1.392 | 704 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03514010 | 14 | 55 | 10 | 4.8 | 2703 | 588 | 0.27 | 0.0086287 |  | 1.399 | 1257 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03514015 | 14 | 55 | 15 | 6.8 | 4438 | 966 | 0.44 | 0.019875 |  | 1.39 | 2058 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03516005 | 14 | 63 | 05 | 2.8 | 1735 | 331 | 0.17 | 0.0083419 |  | 1.392 | 805 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03516010 | 14 | 63 | 10 | 4.8 | 3090 | 589 | 0.31 | 0.012012 |  | 1.399 | 1437 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03516015 | 14 | 63 | 15 | 6.8 | 5073 | 966 | 0.51 | 0.02743 |  | 1.39 | 2352 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03518005 | 14 | 71 | 05 | 2.8 | 1951 | 330 | 0.2 | 0.012393 |  | 1.392 | 905 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03518010 | 14 | 71 | 10 | 4.8 | 3475 | 588 | 0.35 | 0.016094 |  | 1.399 | 1616 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03518015 | 14 | 71 | 15 | 6.8 | 5707 | 966 | 0.57 | 0.035186 |  | 1.39 | 2646 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03520005 | 14 | 78.5 | 05 | 2.8 | 2168 | 330 | 0.22 | 0.016114 |  | 1.392 | 1006 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03520010 | 14 | 78.5 | 10 | 4.8 | 3862 | 589 | 0.39 | 0.020923 |  | 1.399 | 1796 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03520015 | 14 | 78.5 | 15 | 6.8 | 6341 | 966 | 0.63 | 0.044072 |  | 1.39 | 2940 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03522005 | 14 | 86.5 | 05 | 2.8 | 2386 | 331 | 0.24 | 0.020479 |  | 1.392 | 1107 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03522010 | 14 | 86.5 | 10 | 4.8 | 4247 | 588 | 0.42 | 0.025415 |  | 1.399 | 1975 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03522015 | 14 | 86.5 | 15 | 6.8 | 7139 | 989 | 0.71 | 0.057175 |  | 1.39 | 3310 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03524005 | 14 | 94.5 | 05 | 2.8 | 2601 | 330 | 0.26 | 0.025532 |  | 1.392 | 1207 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03524010 | 14 | 94.5 | 10 | 4.8 | 4634 | 589 | 0.46 | 0.031721 |  | 1.399 | 2155 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03524015 | 14 | 94.5 | 15 | 6.8 | 7609 | 966 | 0.76 | 0.067088 |  | 1.39 | 3528 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03526005 | 14 | 102.5 | 05 | 2.8 | 2819 | 330 | 0.28 | 0.031315 |  | 1.392 | 1308 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03526010 | 14 | 102.5 | 10 | 4.8 | 5019 | 588 | 0.5 | 0.038903 |  | 1.399 | 2334 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03526015 | 14 | 102.5 | 15 | 6.8 | 8407 | 986 | 0.84 | 0.083548 |  | 1.39 | 3898 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.03528005 | 14 | 110 | 05 | 2.8 | 3035 | 330 | 0.3 | 0.03787 |  | 1.392 | 1408 | [19 empty] | 0.0009367 | 1.7898 | 2 | 0.0004456
Horizontal Wall | Strada Continuo | STCO.03528010 | 14 | 110 | 10 | 4.8 | 5406 | 588 | 0.54 | 0.047004 |  | 1.399 | 2514 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.03528015 | 14 | 110 | 15 | 6.8 | 8877 | 966 | 0.89 | 0.095853 |  | 1.39 | 4116 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05005010 | 19.5 | 19.5 | 10 | 4.8 | 1162 | 708 | 0.12 | 0.0011777 |  | 1.385 | 538 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05005015 | 19.5 | 19.5 | 15 | 6.8 | 1880 | 1146 | 0.19 | 0.0031316 |  | 1.373 | 867 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05005020 | 19.5 | 19.5 | 20 | 8.7 | 2631 | 1604 | 0.26 | 0.0046274 |  | 1.373 | 1213 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05006010 | 19.5 | 23.5 | 10 | 4.8 | 1396 | 709 | 0.14 | 0.0016922 |  | 1.385 | 646 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05006015 | 19.5 | 23.5 | 15 | 6.8 | 2256 | 1146 | 0.23 | 0.0046896 |  | 1.373 | 1040 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05006020 | 19.5 | 23.5 | 20 | 8.7 | 3156 | 1603 | 0.32 | 0.007115 |  | 1.373 | 1455 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05007010 | 19.5 | 27.5 | 10 | 4.8 | 1627 | 708 | 0.16 | 0.0023206 |  | 1.385 | 753 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05007015 | 19.5 | 27.5 | 15 | 6.8 | 2633 | 1146 | 0.26 | 0.0061227 |  | 1.373 | 1214 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05007020 | 19.5 | 27.5 | 20 | 8.7 | 3683 | 1604 | 0.37 | 0.0096517 |  | 1.373 | 1698 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05008010 | 19.5 | 31.5 | 10 | 4.8 | 1860 | 709 | 0.19 | 0.0034042 |  | 1.385 | 861 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05008015 | 19.5 | 31.5 | 15 | 6.8 | 3008 | 1146 | 0.3 | 0.0083046 |  | 1.373 | 1387 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05008020 | 19.5 | 31.5 | 20 | 8.7 | 4208 | 1603 | 0.42 | 0.012608 |  | 1.373 | 1940 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05009010 | 19.5 | 35.5 | 10 | 4.8 | 2091 | 708 | 0.21 | 0.0043329 |  | 1.385 | 968 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05009015 | 19.5 | 35.5 | 15 | 6.8 | 3386 | 1147 | 0.34 | 0.010855 |  | 1.373 | 1561 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05009020 | 19.5 | 35.5 | 20 | 8.7 | 4735 | 1604 | 0.47 | 0.015994 |  | 1.373 | 2183 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05010010 | 19.5 | 39.5 | 10 | 4.8 | 2324 | 708 | 0.23 | 0.0053996 |  | 1.385 | 1076 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05010015 | 19.5 | 39.5 | 15 | 6.8 | 3761 | 1146 | 0.38 | 0.013786 |  | 1.373 | 1734 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05010020 | 19.5 | 39.5 | 20 | 8.7 | 5259 | 1603 | 0.53 | 0.020575 |  | 1.373 | 2425 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05011010 | 19.5 | 43.5 | 10 | 4.8 | 2558 | 709 | 0.26 | 0.0071199 |  | 1.385 | 1184 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05011015 | 19.5 | 43.5 | 15 | 6.8 | 4136 | 1146 | 0.41 | 0.016325 |  | 1.373 | 1907 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05011020 | 19.5 | 43.5 | 20 | 8.7 | 5786 | 1603 | 0.58 | 0.024932 |  | 1.373 | 2668 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05012010 | 19.5 | 47 | 10 | 4.8 | 2789 | 708 | 0.28 | 0.0085399 |  | 1.385 | 1291 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05012015 | 19.5 | 47 | 15 | 6.8 | 4513 | 1146 | 0.45 | 0.019964 |  | 1.373 | 2081 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05012020 | 19.5 | 47 | 20 | 8.7 | 6311 | 1603 | 0.63 | 0.02975 |  | 1.373 | 2910 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05014010 | 19.5 | 55 | 10 | 4.8 | 3253 | 708 | 0.33 | 0.012571 |  | 1.385 | 1506 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05014015 | 19.5 | 55 | 15 | 6.8 | 5266 | 1146 | 0.53 | 0.028489 |  | 1.373 | 2428 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05014020 | 19.5 | 55 | 20 | 8.7 | 7363 | 1603 | 0.74 | 0.041905 |  | 1.373 | 3395 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05016010 | 19.5 | 63 | 10 | 4.8 | 3720 | 709 | 0.37 | 0.016715 |  | 1.385 | 1722 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05016015 | 19.5 | 63 | 15 | 6.8 | 6016 | 1146 | 0.6 | 0.03753 |  | 1.373 | 2774 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05016020 | 19.5 | 63 | 20 | 8.7 | 8415 | 1603 | 0.84 | 0.055088 |  | 1.373 | 3880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05018010 | 19.5 | 71 | 10 | 4.8 | 4184 | 708 | 0.42 | 0.022597 |  | 1.385 | 1937 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05018015 | 19.5 | 71 | 15 | 6.8 | 6769 | 1146 | 0.68 | 0.049408 |  | 1.373 | 3121 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05018020 | 19.5 | 71 | 20 | 8.7 | 9467 | 1603 | 0.95 | 0.071762 |  | 1.373 | 4365 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05020010 | 19.5 | 78.5 | 10 | 4.8 | 4649 | 709 | 0.46 | 0.028422 |  | 1.385 | 2152 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05020015 | 19.5 | 78.5 | 15 | 6.8 | 7521 | 1146 | 0.75 | 0.061584 |  | 1.373 | 3468 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05020020 | 19.5 | 78.5 | 20 | 8.7 | 10519 | 1603 | 1.05 | 0.089252 |  | 1.373 | 4850 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05022010 | 19.5 | 86.5 | 10 | 4.8 | 5113 | 708 | 0.51 | 0.036401 |  | 1.385 | 2367 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05022015 | 19.5 | 86.5 | 15 | 6.8 | 8274 | 1146 | 0.83 | 0.077102 |  | 1.373 | 3815 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05022020 | 19.5 | 86.5 | 20 | 8.7 | 11571 | 1603 | 1.16 | 0.11075 |  | 1.373 | 5335 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05024010 | 19.5 | 94.5 | 10 | 4.8 | 5578 | 708 | 0.56 | 0.045609 |  | 1.385 | 2582 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05024015 | 19.5 | 94.5 | 15 | 6.8 | 9027 | 1146 | 0.9 | 0.092669 |  | 1.373 | 4162 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05024020 | 19.5 | 94.5 | 20 | 8.7 | 12623 | 1603 | 1.26 | 0.13282 |  | 1.373 | 5820 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05026010 | 19.5 | 102.5 | 10 | 4.8 | 6044 | 709 | 0.6 | 0.054428 |  | 1.385 | 2798 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05026015 | 19.5 | 102.5 | 15 | 6.8 | 9777 | 1146 | 0.98 | 0.1121 |  | 1.373 | 4508 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05026020 | 19.5 | 102.5 | 20 | 8.7 | 13674 | 1603 | 1.37 | 0.15943 |  | 1.373 | 6305 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.05028010 | 19.5 | 110 | 10 | 4.8 | 6509 | 709 | 0.65 | 0.066091 |  | 1.385 | 3013 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.05028015 | 19.5 | 110 | 15 | 6.8 | 10530 | 1146 | 1.05 | 0.1313 |  | 1.373 | 4855 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.05028020 | 19.5 | 110 | 20 | 8.7 | 14726 | 1603 | 1.47 | 0.18636 |  | 1.373 | 6790 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06505010 | 25.5 | 19.5 | 10 | 4.8 | 1315 | 802 | 0.13 | 0.0013751 |  | 1.371 | 606 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06505015 | 25.5 | 19.5 | 15 | 6.8 | 2097 | 1278 | 0.21 | 0.0038149 |  | 1.355 | 961 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06505020 | 25.5 | 19.5 | 20 | 8.7 | 2930 | 1786 | 0.29 | 0.0057444 |  | 1.355 | 1343 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06506010 | 25.5 | 23.5 | 10 | 4.8 | 1578 | 802 | 0.16 | 0.0021885 |  | 1.371 | 727 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06506015 | 25.5 | 23.5 | 15 | 6.8 | 2516 | 1278 | 0.25 | 0.0055254 |  | 1.355 | 1153 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06506020 | 25.5 | 23.5 | 20 | 8.7 | 3515 | 1786 | 0.35 | 0.0084937 |  | 1.355 | 1611 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06507010 | 25.5 | 27.5 | 10 | 4.8 | 1840 | 801 | 0.18 | 0.0029084 |  | 1.371 | 848 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06507015 | 25.5 | 27.5 | 15 | 6.8 | 2934 | 1278 | 0.29 | 0.0075855 |  | 1.355 | 1345 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06507020 | 25.5 | 27.5 | 20 | 8.7 | 4102 | 1786 | 0.41 | 0.011818 |  | 1.355 | 1880 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06508010 | 25.5 | 31.5 | 10 | 4.8 | 2103 | 801 | 0.21 | 0.0041212 |  | 1.371 | 969 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06508015 | 25.5 | 31.5 | 15 | 6.8 | 3356 | 1279 | 0.34 | 0.01061 |  | 1.355 | 1538 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06508020 | 25.5 | 31.5 | 20 | 8.7 | 4686 | 1785 | 0.47 | 0.015734 |  | 1.355 | 2148 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06509010 | 25.5 | 35.5 | 10 | 4.8 | 2366 | 801 | 0.24 | 0.0055865 |  | 1.371 | 1090 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06509015 | 25.5 | 35.5 | 15 | 6.8 | 3774 | 1278 | 0.38 | 0.01349 |  | 1.355 | 1730 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06509020 | 25.5 | 35.5 | 20 | 8.7 | 5273 | 1786 | 0.53 | 0.020256 |  | 1.355 | 2417 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06510010 | 25.5 | 39.5 | 10 | 4.8 | 2628 | 801 | 0.26 | 0.0068133 |  | 1.371 | 1211 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06510015 | 25.5 | 39.5 | 15 | 6.8 | 4193 | 1278 | 0.42 | 0.016757 |  | 1.355 | 1922 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06510020 | 25.5 | 39.5 | 20 | 8.7 | 5858 | 1786 | 0.59 | 0.025397 |  | 1.355 | 2685 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06511010 | 25.5 | 43.5 | 10 | 4.8 | 2891 | 801 | 0.29 | 0.0087536 |  | 1.371 | 1332 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06511015 | 25.5 | 43.5 | 15 | 6.8 | 4612 | 1278 | 0.46 | 0.020423 |  | 1.355 | 2114 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06511020 | 25.5 | 43.5 | 20 | 8.7 | 6445 | 1786 | 0.64 | 0.03024 |  | 1.355 | 2954 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06512010 | 25.5 | 47 | 10 | 4.8 | 3153 | 801 | 0.32 | 0.010987 |  | 1.371 | 1453 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06512015 | 25.5 | 47 | 15 | 6.8 | 5031 | 1278 | 0.5 | 0.024499 |  | 1.355 | 2306 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06512020 | 25.5 | 47 | 20 | 8.7 | 7030 | 1786 | 0.7 | 0.036566 |  | 1.355 | 3222 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06514010 | 25.5 | 55 | 10 | 4.8 | 3679 | 801 | 0.37 | 0.015585 |  | 1.371 | 1695 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06514015 | 25.5 | 55 | 15 | 6.8 | 5871 | 1278 | 0.59 | 0.035066 |  | 1.355 | 2691 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06514020 | 25.5 | 55 | 20 | 8.7 | 8201 | 1785 | 0.82 | 0.051209 |  | 1.355 | 3759 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06516010 | 25.5 | 63 | 10 | 4.8 | 4206 | 801 | 0.42 | 0.021188 |  | 1.371 | 1938 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06516015 | 25.5 | 63 | 15 | 6.8 | 6709 | 1278 | 0.67 | 0.046443 |  | 1.355 | 3075 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06516020 | 25.5 | 63 | 20 | 8.7 | 9373 | 1786 | 0.94 | 0.068589 |  | 1.355 | 4296 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06518010 | 25.5 | 71 | 10 | 4.8 | 4731 | 801 | 0.47 | 0.027867 |  | 1.371 | 2180 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06518015 | 25.5 | 71 | 15 | 6.8 | 7549 | 1278 | 0.75 | 0.059669 |  | 1.355 | 3460 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06518020 | 25.5 | 71 | 20 | 8.7 | 10544 | 1785 | 1.05 | 0.087181 |  | 1.355 | 4833 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06520010 | 25.5 | 78.5 | 10 | 4.8 | 5256 | 801 | 0.53 | 0.03698 |  | 1.371 | 2422 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06520015 | 25.5 | 78.5 | 15 | 6.8 | 8387 | 1278 | 0.84 | 0.076565 |  | 1.355 | 3844 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06520020 | 25.5 | 78.5 | 20 | 8.7 | 11716 | 1786 | 1.17 | 0.11011 |  | 1.355 | 5370 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06522010 | 25.5 | 86.5 | 10 | 4.8 | 5782 | 801 | 0.58 | 0.046199 |  | 1.371 | 2664 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06522015 | 25.5 | 86.5 | 15 | 6.8 | 9307 | 1289 | 0.93 | 0.095891 |  | 1.355 | 4266 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06522020 | 25.5 | 86.5 | 20 | 8.7 | 13001 | 1801 | 1.3 | 0.13811 |  | 1.355 | 5959 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06524010 | 25.5 | 94.5 | 10 | 4.8 | 6307 | 801 | 0.63 | 0.056705 |  | 1.371 | 2906 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06524015 | 25.5 | 94.5 | 15 | 6.8 | 10064 | 1278 | 1.01 | 0.11554 |  | 1.355 | 4613 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06524020 | 25.5 | 94.5 | 20 | 8.7 | 14059 | 1785 | 1.41 | 0.1651 |  | 1.355 | 6444 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06526010 | 25.5 | 102.5 | 10 | 4.8 | 6834 | 801 | 0.68 | 0.068562 |  | 1.371 | 3149 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06526015 | 25.5 | 102.5 | 15 | 6.8 | 10985 | 1288 | 1.1 | 0.13976 |  | 1.355 | 5035 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06526020 | 25.5 | 102.5 | 20 | 8.7 | 15344 | 1799 | 1.53 | 0.19733 |  | 1.355 | 7033 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661
Horizontal Wall | Strada Continuo | STCO.06528010 | 25.5 | 110 | 10 | 4.8 | 7359 | 801 | 0.74 | 0.08391 |  | 1.371 | 3391 | [19 empty] | 0.0003969 | 1.7346 | 2 | 0.00036735
Horizontal Wall | Strada Continuo | STCO.06528015 | 25.5 | 110 | 15 | 6.8 | 11742 | 1278 | 1.17 | 0.16136 |  | 1.355 | 5382 | [19 empty] | 0.0002083 | 1.724 | 2 | 0.00046183
Horizontal Wall | Strada Continuo | STCO.06528020 | 25.5 | 110 | 20 | 8.7 | 16402 | 1785 | 1.64 | 0.23012 |  | 1.355 | 7518 | [19 empty] | 0.0001276 | 1.7219 | 2 | 0.00037661

## PanelPlus
Selection Model 2022-10 | [37 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF | [28 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF | [14 empty] | h(mm) | 0 | [12 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF | [14 empty] | cf_h | 1 | [12 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF | [29 empty] | -10
[11 empty] | *Sound pressure with an assumed room damping of 8dB(A) | [27 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º |  |  |  |  | N-Waarde |  | 75/65/20ºC |  | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  |  |  | 16/18/27ºC
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | BTU/h per foot | Flow in GPM | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | Kolom | 100% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | k1 | n | t | k2 | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | SalesGroup | JagaSourceCode Stnd
Freestanding | Panel Plus Freestanding | PPHF.01210011.333/GR | 4.5 | 39.5 | 11 | 2 | 595 | 181 | 0.06 | 0 |  | 1.224 |  | 261
Freestanding | Panel Plus Freestanding | PPHF.01210022.333/GR | 4.5 | 39.5 | 22 | 3.5 | 1040 | 317 | 0.1 | 0 |  | 1.206 |  | 454
Freestanding | Panel Plus Freestanding | PPHF.01210034.333/GR | 4.5 | 39.5 | 34 | 6.7 | 1589 | 484 | 0.16 | 0 |  | 1.452 |  | 752
Freestanding | Panel Plus Freestanding | PPHF.01212011.333/GR | 4.5 | 47 | 11 | 2 | 713 | 181 | 0.07 | 0 |  | 1.224 |  | 313
Freestanding | Panel Plus Freestanding | PPHF.01212022.333/GR | 4.5 | 47 | 22 | 3.5 | 1249 | 317 | 0.12 | 0 |  | 1.206 |  | 545
Freestanding | Panel Plus Freestanding | PPHF.01212034.333/GR | 4.5 | 47 | 34 | 6.7 | 1908 | 485 | 0.19 | 0 |  | 1.452 |  | 903
Freestanding | Panel Plus Freestanding | PPHF.01214011.333/GR | 4.5 | 55 | 11 | 2 | 832 | 181 | 0.08 | 0 |  | 1.224 |  | 365
Freestanding | Panel Plus Freestanding | PPHF.01214022.333/GR | 4.5 | 55 | 22 | 3.5 | 1455 | 317 | 0.15 | 0 |  | 1.206 |  | 635
Freestanding | Panel Plus Freestanding | PPHF.01214034.333/GR | 4.5 | 55 | 34 | 6.7 | 2225 | 484 | 0.22 | 0 |  | 1.452 |  | 1053
Freestanding | Panel Plus Freestanding | PPHF.01216011.333/GR | 4.5 | 63 | 11 | 2 | 950 | 181 | 0.1 | 0 |  | 1.224 |  | 417
Freestanding | Panel Plus Freestanding | PPHF.01216022.333/GR | 4.5 | 63 | 22 | 3.5 | 1664 | 317 | 0.17 | 0 |  | 1.206 |  | 726
Freestanding | Panel Plus Freestanding | PPHF.01216034.333/GR | 4.5 | 63 | 34 | 6.7 | 2544 | 485 | 0.25 | 0 |  | 1.452 |  | 1204
Freestanding | Panel Plus Freestanding | PPHF.01218011.333/GR | 4.5 | 71 | 11 | 2 | 1068 | 181 | 0.11 | 0 |  | 1.224 |  | 469
Freestanding | Panel Plus Freestanding | PPHF.01218022.333/GR | 4.5 | 71 | 22 | 3.5 | 1872 | 317 | 0.19 | 0 |  | 1.206 |  | 817
Freestanding | Panel Plus Freestanding | PPHF.01218034.333/GR | 4.5 | 71 | 34 | 6.7 | 2861 | 484 | 0.29 | 0 |  | 1.452 |  | 1354
Freestanding | Panel Plus Freestanding | PPHF.01220011.333/GR | 4.5 | 78.5 | 11 | 2 | 1187 | 181 | 0.12 | 0 |  | 1.224 |  | 521
Freestanding | Panel Plus Freestanding | PPHF.01220022.333/GR | 4.5 | 78.5 | 22 | 3.5 | 2081 | 317 | 0.21 | 0 |  | 1.206 |  | 908
Freestanding | Panel Plus Freestanding | PPHF.01220034.333/GR | 4.5 | 78.5 | 34 | 6.7 | 3180 | 485 | 0.32 | 0 |  | 1.452 |  | 1505
Freestanding | Panel Plus Freestanding | PPHF.01222011.333/GR | 4.5 | 86.5 | 11 | 2 | 1305 | 181 | 0.13 | 0 |  | 1.224 |  | 573
Freestanding | Panel Plus Freestanding | PPHF.01222022.333/GR | 4.5 | 86.5 | 22 | 3.5 | 2287 | 317 | 0.23 | 0 |  | 1.206 |  | 998
Freestanding | Panel Plus Freestanding | PPHF.01222034.333/GR | 4.5 | 86.5 | 34 | 6.7 | 3497 | 484 | 0.35 | 0 |  | 1.452 |  | 1655
Freestanding | Panel Plus Freestanding | PPHF.01224011.333/GR | 4.5 | 94.5 | 11 | 2 | 1424 | 181 | 0.14 | 0 |  | 1.224 |  | 625
Freestanding | Panel Plus Freestanding | PPHF.01224022.333/GR | 4.5 | 94.5 | 22 | 3.5 | 2496 | 317 | 0.25 | 0 |  | 1.206 |  | 1089
Freestanding | Panel Plus Freestanding | PPHF.01224034.333/GR | 4.5 | 94.5 | 34 | 6.7 | 3816 | 485 | 0.38 | 0 |  | 1.452 |  | 1806
Freestanding | Panel Plus Freestanding | PPHF.01226011.333/GR | 4.5 | 102.5 | 11 | 2 | 1542 | 181 | 0.15 | 0 |  | 1.224 |  | 677
Freestanding | Panel Plus Freestanding | PPHF.01226022.333/GR | 4.5 | 102.5 | 22 | 3.5 | 2704 | 317 | 0.27 | 0 |  | 1.206 |  | 1180
Freestanding | Panel Plus Freestanding | PPHF.01226034.333/GR | 4.5 | 102.5 | 34 | 6.7 | 4133 | 485 | 0.41 | 0 |  | 1.452 |  | 1956
Freestanding | Panel Plus Freestanding | PPHF.01228011.333/GR | 4.5 | 110 | 11 | 2 | 1661 | 181 | 0.17 | 0 |  | 1.224 |  | 729
Freestanding | Panel Plus Freestanding | PPHF.01228022.333/GR | 4.5 | 110 | 22 | 3.5 | 2913 | 317 | 0.29 | 0 |  | 1.206 |  | 1271
Freestanding | Panel Plus Freestanding | PPHF.01228034.333/GR | 4.5 | 110 | 34 | 6.7 | 4450 | 484 | 0.45 | 0 |  | 1.452 |  | 2106
Freestanding | Panel Plus Freestanding | PPHF.01230011.333/GR | 4.5 | 118 | 11 | 2 | 1782 | 181 | 0.18 | 0 |  | 1.224 |  | 782
Freestanding | Panel Plus Freestanding | PPHF.01230022.333/GR | 4.5 | 118 | 22 | 3.5 | 3119 | 317 | 0.31 | 0 |  | 1.206 |  | 1361
Freestanding | Panel Plus Freestanding | PPHF.01230034.333/GR | 4.5 | 118 | 34 | 6.7 | 4769 | 485 | 0.48 | 0 |  | 1.452 |  | 2257
Freestanding | Panel Plus Freestanding | PPHF.01232011.333/GR | 4.5 | 126 | 11 | 2 | 1900 | 181 | 0.19 | 0 |  | 1.224 |  | 834
Freestanding | Panel Plus Freestanding | PPHF.01232022.333/GR | 4.5 | 126 | 22 | 3.5 | 3328 | 317 | 0.33 | 0 |  | 1.206 |  | 1452
Freestanding | Panel Plus Freestanding | PPHF.01232034.333/GR | 4.5 | 126 | 34 | 6.7 | 5086 | 484 | 0.51 | 0 |  | 1.452 |  | 2407
Freestanding | Panel Plus Freestanding | PPHF.01234011.333/GR | 4.5 | 134 | 11 | 2 | 2018 | 181 | 0.2 | 0 |  | 1.224 |  | 886
Freestanding | Panel Plus Freestanding | PPHF.01234022.333/GR | 4.5 | 134 | 22 | 3.5 | 3536 | 317 | 0.35 | 0 |  | 1.206 |  | 1543
Freestanding | Panel Plus Freestanding | PPHF.01234034.333/GR | 4.5 | 134 | 34 | 6.7 | 5405 | 485 | 0.54 | 0 |  | 1.452 |  | 2558
Freestanding | Panel Plus Freestanding | PPHF.01236011.333/GR | 4.5 | 141.5 | 11 | 2 | 2137 | 181 | 0.21 | 0 |  | 1.224 |  | 938
Freestanding | Panel Plus Freestanding | PPHF.01236022.333/GR | 4.5 | 141.5 | 22 | 3.5 | 3745 | 317 | 0.37 | 0 |  | 1.206 |  | 1634
Freestanding | Panel Plus Freestanding | PPHF.01236034.333/GR | 4.5 | 141.5 | 34 | 6.7 | 5722 | 484 | 0.57 | 0 |  | 1.452 |  | 2708
Freestanding | Panel Plus Freestanding | PPHF.01238011.333/GR | 4.5 | 149.5 | 11 | 2 | 2255 | 181 | 0.23 | 0 |  | 1.224 |  | 990
Freestanding | Panel Plus Freestanding | PPHF.01238022.333/GR | 4.5 | 149.5 | 22 | 3.5 | 3951 | 317 | 0.4 | 0 |  | 1.206 |  | 1724
Freestanding | Panel Plus Freestanding | PPHF.01238034.333/GR | 4.5 | 149.5 | 34 | 6.7 | 6041 | 485 | 0.6 | 0 |  | 1.452 |  | 2859
Freestanding | Panel Plus Freestanding | PPHF.01242011.333/GR | 4.5 | 165.5 | 11 | 2 | 2492 | 181 | 0.25 | 0 |  | 1.224 |  | 1094
Freestanding | Panel Plus Freestanding | PPHF.01242022.333/GR | 4.5 | 165.5 | 22 | 3.5 | 4368 | 317 | 0.44 | 0 |  | 1.206 |  | 1906
Freestanding | Panel Plus Freestanding | PPHF.01242034.333/GR | 4.5 | 165.5 | 34 | 6.7 | 6677 | 485 | 0.67 | 0 |  | 1.452 |  | 3160
Freestanding | Panel Plus Freestanding | PPHF.01246011.333/GR | 4.5 | 181 | 11 | 2 | 2729 | 181 | 0.27 | 0 |  | 1.224 |  | 1198
Freestanding | Panel Plus Freestanding | PPHF.01246022.333/GR | 4.5 | 181 | 22 | 3.5 | 4783 | 317 | 0.48 | 0 |  | 1.206 |  | 2087
Freestanding | Panel Plus Freestanding | PPHF.01246034.333/GR | 4.5 | 181 | 34 | 6.7 | 7313 | 485 | 0.73 | 0 |  | 1.452 |  | 3461
Freestanding | Panel Plus Freestanding | PPHF.01810011.333/GR | 7 | 39.5 | 11 | 2 | 879 | 268 | 0.09 | 0 |  | 1.248 |  | 389
Freestanding | Panel Plus Freestanding | PPHF.01810022.333/GR | 7 | 39.5 | 22 | 3.5 | 1368 | 417 | 0.14 | 0 |  | 1.349 |  | 626
Freestanding | Panel Plus Freestanding | PPHF.01810034.333/GR | 7 | 39.5 | 34 | 6.7 | 2409 | 734 | 0.24 | 0 |  | 1.452 |  | 1140
Freestanding | Panel Plus Freestanding | PPHF.01812011.333/GR | 7 | 47 | 11 | 2 | 1053 | 267 | 0.11 | 0 |  | 1.248 |  | 466
Freestanding | Panel Plus Freestanding | PPHF.01812022.333/GR | 7 | 47 | 22 | 3.5 | 1642 | 417 | 0.16 | 0 |  | 1.349 |  | 751
Freestanding | Panel Plus Freestanding | PPHF.01812034.333/GR | 7 | 47 | 34 | 6.7 | 2893 | 735 | 0.29 | 0 |  | 1.452 |  | 1369
Freestanding | Panel Plus Freestanding | PPHF.01814011.333/GR | 7 | 55 | 11 | 2 | 1230 | 268 | 0.12 | 0 |  | 1.248 |  | 544
Freestanding | Panel Plus Freestanding | PPHF.01814022.333/GR | 7 | 55 | 22 | 3.5 | 1915 | 417 | 0.19 | 0 |  | 1.349 |  | 876
Freestanding | Panel Plus Freestanding | PPHF.01814034.333/GR | 7 | 55 | 34 | 6.7 | 3374 | 735 | 0.34 | 0 |  | 1.452 |  | 1597
Freestanding | Panel Plus Freestanding | PPHF.01816011.333/GR | 7 | 63 | 11 | 2 | 1406 | 268 | 0.14 | 0 |  | 1.248 |  | 622
Freestanding | Panel Plus Freestanding | PPHF.01816022.333/GR | 7 | 63 | 22 | 3.5 | 2188 | 417 | 0.22 | 0 |  | 1.349 |  | 1001
Freestanding | Panel Plus Freestanding | PPHF.01816034.333/GR | 7 | 63 | 34 | 6.7 | 3856 | 735 | 0.39 | 0 |  | 1.452 |  | 1825
Freestanding | Panel Plus Freestanding | PPHF.01818011.333/GR | 7 | 71 | 11 | 2 | 1580 | 268 | 0.16 | 0 |  | 1.248 |  | 699
Freestanding | Panel Plus Freestanding | PPHF.01818022.333/GR | 7 | 71 | 22 | 3.5 | 2462 | 417 | 0.25 | 0 |  | 1.349 |  | 1126
Freestanding | Panel Plus Freestanding | PPHF.01818034.333/GR | 7 | 71 | 34 | 6.7 | 4338 | 735 | 0.43 | 0 |  | 1.452 |  | 2053
Freestanding | Panel Plus Freestanding | PPHF.01820011.333/GR | 7 | 78.5 | 11 | 2 | 1756 | 268 | 0.18 | 0 |  | 1.248 |  | 777
Freestanding | Panel Plus Freestanding | PPHF.01820022.333/GR | 7 | 78.5 | 22 | 3.5 | 2737 | 417 | 0.27 | 0 |  | 1.349 |  | 1252
Freestanding | Panel Plus Freestanding | PPHF.01820034.333/GR | 7 | 78.5 | 34 | 6.7 | 4820 | 735 | 0.48 | 0 |  | 1.452 |  | 2281
Freestanding | Panel Plus Freestanding | PPHF.01822011.333/GR | 7 | 86.5 | 11 | 2 | 1932 | 268 | 0.19 | 0 |  | 1.248 |  | 855
Freestanding | Panel Plus Freestanding | PPHF.01822022.333/GR | 7 | 86.5 | 22 | 3.5 | 3010 | 417 | 0.3 | 0 |  | 1.349 |  | 1377
Freestanding | Panel Plus Freestanding | PPHF.01822034.333/GR | 7 | 86.5 | 34 | 6.7 | 5302 | 735 | 0.53 | 0 |  | 1.452 |  | 2509
Freestanding | Panel Plus Freestanding | PPHF.01824011.333/GR | 7 | 94.5 | 11 | 2 | 2106 | 267 | 0.21 | 0 |  | 1.248 |  | 932
Freestanding | Panel Plus Freestanding | PPHF.01824022.333/GR | 7 | 94.5 | 22 | 3.5 | 3283 | 417 | 0.33 | 0 |  | 1.349 |  | 1502
Freestanding | Panel Plus Freestanding | PPHF.01824034.333/GR | 7 | 94.5 | 34 | 6.7 | 5783 | 734 | 0.58 | 0 |  | 1.452 |  | 2737
Freestanding | Panel Plus Freestanding | PPHF.01826011.333/GR | 7 | 102.5 | 11 | 2 | 2283 | 268 | 0.23 | 0 |  | 1.248 |  | 1010
Freestanding | Panel Plus Freestanding | PPHF.01826022.333/GR | 7 | 102.5 | 22 | 3.5 | 3557 | 417 | 0.36 | 0 |  | 1.349 |  | 1627
Freestanding | Panel Plus Freestanding | PPHF.01826034.333/GR | 7 | 102.5 | 34 | 6.7 | 6265 | 734 | 0.63 | 0 |  | 1.452 |  | 2965
Freestanding | Panel Plus Freestanding | PPHF.01828011.333/GR | 7 | 110 | 11 | 2 | 2459 | 268 | 0.25 | 0 |  | 1.248 |  | 1088
Freestanding | Panel Plus Freestanding | PPHF.01828022.333/GR | 7 | 110 | 22 | 3.5 | 3830 | 417 | 0.38 | 0 |  | 1.349 |  | 1752
Freestanding | Panel Plus Freestanding | PPHF.01828034.333/GR | 7 | 110 | 34 | 6.7 | 6747 | 734 | 0.67 | 0 |  | 1.452 |  | 3193
Freestanding | Panel Plus Freestanding | PPHF.01830011.333/GR | 7 | 118 | 11 | 2 | 2635 | 268 | 0.26 | 0 |  | 1.248 |  | 1166
Freestanding | Panel Plus Freestanding | PPHF.01830022.333/GR | 7 | 118 | 22 | 3.5 | 4103 | 417 | 0.41 | 0 |  | 1.349 |  | 1877
Freestanding | Panel Plus Freestanding | PPHF.01830034.333/GR | 7 | 118 | 34 | 6.7 | 7229 | 734 | 0.72 | 0 |  | 1.452 |  | 3421
Freestanding | Panel Plus Freestanding | PPHF.01832011.333/GR | 7 | 126 | 11 | 2 | 2809 | 268 | 0.28 | 0 |  | 1.248 |  | 1243
Freestanding | Panel Plus Freestanding | PPHF.01832022.333/GR | 7 | 126 | 22 | 3.5 | 4377 | 417 | 0.44 | 0 |  | 1.349 |  | 2002
Freestanding | Panel Plus Freestanding | PPHF.01832034.333/GR | 7 | 126 | 34 | 6.7 | 7710 | 734 | 0.77 | 0 |  | 1.452 |  | 3649
Freestanding | Panel Plus Freestanding | PPHF.01834011.333/GR | 7 | 134 | 11 | 2 | 2986 | 268 | 0.3 | 0 |  | 1.248 |  | 1321
Freestanding | Panel Plus Freestanding | PPHF.01834022.333/GR | 7 | 134 | 22 | 3.5 | 4652 | 417 | 0.47 | 0 |  | 1.349 |  | 2128
Freestanding | Panel Plus Freestanding | PPHF.01834034.333/GR | 7 | 134 | 34 | 6.7 | 8192 | 734 | 0.82 | 0 |  | 1.452 |  | 3877
Freestanding | Panel Plus Freestanding | PPHF.01836011.333/GR | 7 | 141.5 | 11 | 2 | 3162 | 268 | 0.32 | 0 |  | 1.248 |  | 1399
Freestanding | Panel Plus Freestanding | PPHF.01836022.333/GR | 7 | 141.5 | 22 | 3.5 | 4925 | 417 | 0.49 | 0 |  | 1.349 |  | 2253
Freestanding | Panel Plus Freestanding | PPHF.01836034.333/GR | 7 | 141.5 | 34 | 6.7 | 8676 | 735 | 0.87 | 0 |  | 1.452 |  | 4106
Freestanding | Panel Plus Freestanding | PPHF.01838011.333/GR | 7 | 149.5 | 11 | 2 | 3336 | 268 | 0.33 | 0 |  | 1.248 |  | 1476
Freestanding | Panel Plus Freestanding | PPHF.01838022.333/GR | 7 | 149.5 | 22 | 3.5 | 5198 | 417 | 0.52 | 0 |  | 1.349 |  | 2378
Freestanding | Panel Plus Freestanding | PPHF.01838034.333/GR | 7 | 149.5 | 34 | 6.7 | 9158 | 735 | 0.92 | 0 |  | 1.452 |  | 4334
Freestanding | Panel Plus Freestanding | PPHF.01842011.333/GR | 7 | 165.5 | 11 | 2 | 3689 | 268 | 0.37 | 0 |  | 1.248 |  | 1632
Freestanding | Panel Plus Freestanding | PPHF.01842022.333/GR | 7 | 165.5 | 22 | 3.5 | 5745 | 417 | 0.57 | 0 |  | 1.349 |  | 2628
Freestanding | Panel Plus Freestanding | PPHF.01842034.333/GR | 7 | 165.5 | 34 | 6.7 | 10121 | 734 | 1.01 | 0 |  | 1.452 |  | 4790
Freestanding | Panel Plus Freestanding | PPHF.01846011.333/GR | 7 | 181 | 11 | 2 | 4039 | 268 | 0.4 | 0 |  | 1.248 |  | 1787
Freestanding | Panel Plus Freestanding | PPHF.02406011.333/GR | 9.5 | 23.5 | 11 | 2 | 644 | 327 | 0.06 | 0 |  | 1.248 |  | 285
Freestanding | Panel Plus Freestanding | PPHF.02406022.333/GR | 9.5 | 23.5 | 22 | 3.5 | 1043 | 530 | 0.1 | 0 |  | 1.349 |  | 477
Freestanding | Panel Plus Freestanding | PPHF.02406034.333/GR | 9.5 | 23.5 | 34 | 6.7 | 1849 | 939 | 0.18 | 0 |  | 1.452 |  | 875
Freestanding | Panel Plus Freestanding | PPHF.02408011.333/GR | 9.5 | 31.5 | 11 | 2 | 859 | 327 | 0.09 | 0 |  | 1.248 |  | 380
Freestanding | Panel Plus Freestanding | PPHF.02408022.333/GR | 9.5 | 31.5 | 22 | 3.5 | 1390 | 530 | 0.14 | 0 |  | 1.349 |  | 636
Freestanding | Panel Plus Freestanding | PPHF.02408034.333/GR | 9.5 | 31.5 | 34 | 6.7 | 2464 | 939 | 0.25 | 0 |  | 1.452 |  | 1166
Freestanding | Panel Plus Freestanding | PPHF.02410011.333/GR | 9.5 | 39.5 | 11 | 2 | 1074 | 327 | 0.11 | 0 |  | 1.248 |  | 475
Freestanding | Panel Plus Freestanding | PPHF.02410022.333/GR | 9.5 | 39.5 | 22 | 3.5 | 1736 | 529 | 0.17 | 0 |  | 1.349 |  | 794
Freestanding | Panel Plus Freestanding | PPHF.02410034.333/GR | 9.5 | 39.5 | 34 | 6.7 | 3081 | 939 | 0.31 | 0 |  | 1.452 |  | 1458
Freestanding | Panel Plus Freestanding | PPHF.02412011.333/GR | 9.5 | 47 | 11 | 2 | 1288 | 327 | 0.13 | 0 |  | 1.248 |  | 570
Freestanding | Panel Plus Freestanding | PPHF.02412022.333/GR | 9.5 | 47 | 22 | 3.5 | 2083 | 529 | 0.21 | 0 |  | 1.349 |  | 953
Freestanding | Panel Plus Freestanding | PPHF.02412034.333/GR | 9.5 | 47 | 34 | 6.7 | 3696 | 939 | 0.37 | 0 |  | 1.452 |  | 1749
Freestanding | Panel Plus Freestanding | PPHF.02414011.333/GR | 9.5 | 55 | 11 | 2 | 1503 | 327 | 0.15 | 0 |  | 1.248 |  | 665
Freestanding | Panel Plus Freestanding | PPHF.02414022.333/GR | 9.5 | 55 | 22 | 3.5 | 2431 | 529 | 0.24 | 0 |  | 1.349 |  | 1112
Freestanding | Panel Plus Freestanding | PPHF.02414034.333/GR | 9.5 | 55 | 34 | 6.7 | 4313 | 939 | 0.43 | 0 |  | 1.452 |  | 2041
Freestanding | Panel Plus Freestanding | PPHF.02416011.333/GR | 9.5 | 63 | 11 | 2 | 1718 | 327 | 0.17 | 0 |  | 1.248 |  | 760
Freestanding | Panel Plus Freestanding | PPHF.02416022.333/GR | 9.5 | 63 | 22 | 3.5 | 2779 | 529 | 0.28 | 0 |  | 1.349 |  | 1271
Freestanding | Panel Plus Freestanding | PPHF.02416034.333/GR | 9.5 | 63 | 34 | 6.7 | 4928 | 939 | 0.49 | 0 |  | 1.452 |  | 2332
Freestanding | Panel Plus Freestanding | PPHF.02418011.333/GR | 9.5 | 71 | 11 | 2 | 1932 | 327 | 0.19 | 0 |  | 1.248 |  | 855
Freestanding | Panel Plus Freestanding | PPHF.02418022.333/GR | 9.5 | 71 | 22 | 3.5 | 3126 | 529 | 0.31 | 0 |  | 1.349 |  | 1430
Freestanding | Panel Plus Freestanding | PPHF.02418034.333/GR | 9.5 | 71 | 34 | 6.7 | 5545 | 939 | 0.55 | 0 |  | 1.452 |  | 2624
Freestanding | Panel Plus Freestanding | PPHF.02420011.333/GR | 9.5 | 78.5 | 11 | 2 | 2147 | 327 | 0.21 | 0 |  | 1.248 |  | 950
Freestanding | Panel Plus Freestanding | PPHF.02420022.333/GR | 9.5 | 78.5 | 22 | 3.5 | 3474 | 529 | 0.35 | 0 |  | 1.349 |  | 1589
Freestanding | Panel Plus Freestanding | PPHF.02420034.333/GR | 9.5 | 78.5 | 34 | 6.7 | 6159 | 939 | 0.62 | 0 |  | 1.452 |  | 2915
Freestanding | Panel Plus Freestanding | PPHF.02422011.333/GR | 9.5 | 86.5 | 11 | 2 | 2362 | 327 | 0.24 | 0 |  | 1.248 |  | 1045
Freestanding | Panel Plus Freestanding | PPHF.02422022.333/GR | 9.5 | 86.5 | 22 | 3.5 | 3821 | 529 | 0.38 | 0 |  | 1.349 |  | 1748
Freestanding | Panel Plus Freestanding | PPHF.02422034.333/GR | 9.5 | 86.5 | 34 | 6.7 | 6776 | 939 | 0.68 | 0 |  | 1.452 |  | 3207
Freestanding | Panel Plus Freestanding | PPHF.02424011.333/GR | 9.5 | 94.5 | 11 | 2 | 2577 | 327 | 0.26 | 0 |  | 1.248 |  | 1140
Freestanding | Panel Plus Freestanding | PPHF.02424022.333/GR | 9.5 | 94.5 | 22 | 3.5 | 4169 | 529 | 0.42 | 0 |  | 1.349 |  | 1907
Freestanding | Panel Plus Freestanding | PPHF.02424034.333/GR | 9.5 | 94.5 | 34 | 6.7 | 7391 | 939 | 0.74 | 0 |  | 1.452 |  | 3498
Freestanding | Panel Plus Freestanding | PPHF.02426011.333/GR | 9.5 | 102.5 | 11 | 2 | 2791 | 327 | 0.28 | 0 |  | 1.248 |  | 1235
Freestanding | Panel Plus Freestanding | PPHF.02426022.333/GR | 9.5 | 102.5 | 22 | 3.5 | 4514 | 529 | 0.45 | 0 |  | 1.349 |  | 2065
Freestanding | Panel Plus Freestanding | PPHF.02426034.333/GR | 9.5 | 102.5 | 34 | 6.7 | 8008 | 939 | 0.8 | 0 |  | 1.452 |  | 3790
Freestanding | Panel Plus Freestanding | PPHF.02428011.333/GR | 9.5 | 110 | 11 | 2 | 3006 | 327 | 0.3 | 0 |  | 1.248 |  | 1330
Freestanding | Panel Plus Freestanding | PPHF.02428022.333/GR | 9.5 | 110 | 22 | 3.5 | 4862 | 529 | 0.49 | 0 |  | 1.349 |  | 2224
Freestanding | Panel Plus Freestanding | PPHF.02428034.333/GR | 9.5 | 110 | 34 | 6.7 | 8623 | 939 | 0.86 | 0 |  | 1.452 |  | 4081
Freestanding | Panel Plus Freestanding | PPHF.02430011.333/GR | 9.5 | 118 | 11 | 2 | 3221 | 327 | 0.32 | 0 |  | 1.248 |  | 1425
Freestanding | Panel Plus Freestanding | PPHF.02430022.333/GR | 9.5 | 118 | 22 | 3.5 | 5209 | 529 | 0.52 | 0 |  | 1.349 |  | 2383
Freestanding | Panel Plus Freestanding | PPHF.02430034.333/GR | 9.5 | 118 | 34 | 6.7 | 9240 | 939 | 0.92 | 0 |  | 1.452 |  | 4373
Freestanding | Panel Plus Freestanding | PPHF.03106011.333/GR | 12 | 23.5 | 11 | 2 | 755 | 384 | 0.08 | 0 |  | 1.248 |  | 334
Freestanding | Panel Plus Freestanding | PPHF.03106022.333/GR | 12 | 23.5 | 22 | 3.5 | 1248 | 634 | 0.12 | 0 |  | 1.349 |  | 571
Freestanding | Panel Plus Freestanding | PPHF.03106034.333/GR | 12 | 23.5 | 34 | 6.7 | 2152 | 1093 | 0.22 | 0 |  | 1.451 |  | 1018
Freestanding | Panel Plus Freestanding | PPHF.03108011.333/GR | 12 | 31.5 | 11 | 2 | 1006 | 383 | 0.1 | 0 |  | 1.248 |  | 445
Freestanding | Panel Plus Freestanding | PPHF.03108022.333/GR | 12 | 31.5 | 22 | 3.5 | 1664 | 634 | 0.17 | 0 |  | 1.349 |  | 761
Freestanding | Panel Plus Freestanding | PPHF.03108034.333/GR | 12 | 31.5 | 34 | 6.7 | 2868 | 1093 | 0.29 | 0 |  | 1.451 |  | 1357
Freestanding | Panel Plus Freestanding | PPHF.03110011.333/GR | 12 | 39.5 | 11 | 2 | 1257 | 383 | 0.13 | 0 |  | 1.248 |  | 556
Freestanding | Panel Plus Freestanding | PPHF.03110022.333/GR | 12 | 39.5 | 22 | 3.5 | 2079 | 634 | 0.21 | 0 |  | 1.349 |  | 951
Freestanding | Panel Plus Freestanding | PPHF.03110034.333/GR | 12 | 39.5 | 34 | 6.7 | 3587 | 1093 | 0.36 | 0 |  | 1.451 |  | 1697
Freestanding | Panel Plus Freestanding | PPHF.03112011.333/GR | 12 | 47 | 11 | 2 | 1510 | 384 | 0.15 | 0 |  | 1.248 |  | 668
Freestanding | Panel Plus Freestanding | PPHF.03112022.333/GR | 12 | 47 | 22 | 3.5 | 2496 | 634 | 0.25 | 0 |  | 1.349 |  | 1142
Freestanding | Panel Plus Freestanding | PPHF.03112034.333/GR | 12 | 47 | 34 | 6.7 | 4304 | 1093 | 0.43 | 0 |  | 1.451 |  | 2036
Freestanding | Panel Plus Freestanding | PPHF.03114011.333/GR | 12 | 55 | 11 | 2 | 1761 | 383 | 0.18 | 0 |  | 1.248 |  | 779
Freestanding | Panel Plus Freestanding | PPHF.03114022.333/GR | 12 | 55 | 22 | 3.5 | 2912 | 634 | 0.29 | 0 |  | 1.349 |  | 1332
Freestanding | Panel Plus Freestanding | PPHF.03114034.333/GR | 12 | 55 | 34 | 6.7 | 5020 | 1093 | 0.5 | 0 |  | 1.451 |  | 2375
Freestanding | Panel Plus Freestanding | PPHF.03116011.333/GR | 12 | 63 | 11 | 2 | 2012 | 383 | 0.2 | 0 |  | 1.248 |  | 890
Freestanding | Panel Plus Freestanding | PPHF.03116022.333/GR | 12 | 63 | 22 | 3.5 | 3327 | 634 | 0.33 | 0 |  | 1.349 |  | 1522
Freestanding | Panel Plus Freestanding | PPHF.03116034.333/GR | 12 | 63 | 34 | 6.7 | 5739 | 1093 | 0.57 | 0 |  | 1.451 |  | 2715
Freestanding | Panel Plus Freestanding | PPHF.03118011.333/GR | 12 | 71 | 11 | 2 | 2262 | 383 | 0.23 | 0 |  | 1.248 |  | 1001
Freestanding | Panel Plus Freestanding | PPHF.03118022.333/GR | 12 | 71 | 22 | 3.5 | 3745 | 634 | 0.37 | 0 |  | 1.349 |  | 1713
Freestanding | Panel Plus Freestanding | PPHF.03118034.333/GR | 12 | 71 | 34 | 6.7 | 6455 | 1093 | 0.65 | 0 |  | 1.451 |  | 3054
Freestanding | Panel Plus Freestanding | PPHF.03120011.333/GR | 12 | 78.5 | 11 | 2 | 2516 | 383 | 0.25 | 0 |  | 1.248 |  | 1113
Freestanding | Panel Plus Freestanding | PPHF.03120022.333/GR | 12 | 78.5 | 22 | 3.5 | 4160 | 634 | 0.42 | 0 |  | 1.349 |  | 1903
Freestanding | Panel Plus Freestanding | PPHF.03120034.333/GR | 12 | 78.5 | 34 | 6.7 | 7172 | 1093 | 0.72 | 0 |  | 1.451 |  | 3393
Freestanding | Panel Plus Freestanding | PPHF.03122011.333/GR | 12 | 86.5 | 11 | 2 | 2766 | 383 | 0.28 | 0 |  | 1.248 |  | 1224
Freestanding | Panel Plus Freestanding | PPHF.03122022.333/GR | 12 | 86.5 | 22 | 3.5 | 4575 | 634 | 0.46 | 0 |  | 1.349 |  | 2093
Freestanding | Panel Plus Freestanding | PPHF.03122034.333/GR | 12 | 86.5 | 34 | 6.7 | 7890 | 1093 | 0.79 | 0 |  | 1.451 |  | 3733
Freestanding | Panel Plus Freestanding | PPHF.03124011.333/GR | 12 | 94.5 | 11 | 2 | 3017 | 383 | 0.3 | 0 |  | 1.248 |  | 1335
Freestanding | Panel Plus Freestanding | PPHF.03124022.333/GR | 12 | 94.5 | 22 | 3.5 | 4991 | 634 | 0.5 | 0 |  | 1.349 |  | 2283
Freestanding | Panel Plus Freestanding | PPHF.03124034.333/GR | 12 | 94.5 | 34 | 6.7 | 8607 | 1093 | 0.86 | 0 |  | 1.451 |  | 4072
Freestanding | Panel Plus Freestanding | PPHF.03126011.333/GR | 12 | 102.5 | 11 | 2 | 3268 | 383 | 0.33 | 0 |  | 1.248 |  | 1446
Freestanding | Panel Plus Freestanding | PPHF.03126022.333/GR | 12 | 102.5 | 22 | 3.5 | 5408 | 634 | 0.54 | 0 |  | 1.349 |  | 2474
Freestanding | Panel Plus Freestanding | PPHF.03126034.333/GR | 12 | 102.5 | 34 | 6.7 | 9324 | 1093 | 0.93 | 0 |  | 1.451 |  | 4411
Freestanding | Panel Plus Freestanding | PPHF.03128011.333/GR | 12 | 110 | 11 | 2 | 3521 | 383 | 0.35 | 0 |  | 1.248 |  | 1558
Freestanding | Panel Plus Freestanding | PPHF.03128022.333/GR | 12 | 110 | 22 | 3.5 | 5824 | 634 | 0.58 | 0 |  | 1.349 |  | 2664
Freestanding | Panel Plus Freestanding | PPHF.03128034.333/GR | 12 | 110 | 34 | 6.7 | 10042 | 1093 | 1 | 0 |  | 1.451 |  | 4751
Freestanding | Panel Plus Freestanding | PPHF.03130011.333/GR | 12 | 118 | 11 | 2 | 3772 | 383 | 0.38 | 0 |  | 1.248 |  | 1669
Freestanding | Panel Plus Freestanding | PPHF.03130022.333/GR | 12 | 118 | 22 | 3.5 | 6239 | 634 | 0.62 | 0 |  | 1.349 |  | 2854
Freestanding | Panel Plus Freestanding | PPHF.03130034.333/GR | 12 | 118 | 34 | 6.7 | 10759 | 1093 | 1.08 | 0 |  | 1.451 |  | 5090
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01210011.333/GR | 4.5 | 39.5 | 11 | 2 | 595 | 181 | 0.06 | 0 |  | 1.224 |  | 261
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01210022.333/GR | 4.5 | 39.5 | 22 | 3.5 | 1040 | 317 | 0.1 | 0 |  | 1.206 |  | 454
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01210034.333/GR | 4.5 | 39.5 | 34 | 6.7 | 1589 | 484 | 0.16 | 0 |  | 1.452 |  | 752
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01212011.333/GR | 4.5 | 47 | 11 | 2 | 713 | 181 | 0.07 | 0 |  | 1.224 |  | 313
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01212022.333/GR | 4.5 | 47 | 22 | 3.5 | 1249 | 317 | 0.12 | 0 |  | 1.206 |  | 545
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01212034.333/GR | 4.5 | 47 | 34 | 6.7 | 1908 | 485 | 0.19 | 0 |  | 1.452 |  | 903
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01214011.333/GR | 4.5 | 55 | 11 | 2 | 832 | 181 | 0.08 | 0 |  | 1.224 |  | 365
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01214022.333/GR | 4.5 | 55 | 22 | 3.5 | 1455 | 317 | 0.15 | 0 |  | 1.206 |  | 635
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01214034.333/GR | 4.5 | 55 | 34 | 6.7 | 2225 | 484 | 0.22 | 0 |  | 1.452 |  | 1053
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01216011.333/GR | 4.5 | 63 | 11 | 2 | 950 | 181 | 0.1 | 0 |  | 1.224 |  | 417
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01216022.333/GR | 4.5 | 63 | 22 | 3.5 | 1664 | 317 | 0.17 | 0 |  | 1.206 |  | 726
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01216034.333/GR | 4.5 | 63 | 34 | 6.7 | 2544 | 485 | 0.25 | 0 |  | 1.452 |  | 1204
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01218011.333/GR | 4.5 | 71 | 11 | 2 | 1068 | 181 | 0.11 | 0 |  | 1.224 |  | 469
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01218022.333/GR | 4.5 | 71 | 22 | 3.5 | 1872 | 317 | 0.19 | 0 |  | 1.206 |  | 817
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01218034.333/GR | 4.5 | 71 | 34 | 6.7 | 2861 | 484 | 0.29 | 0 |  | 1.452 |  | 1354
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01220011.333/GR | 4.5 | 78.5 | 11 | 2 | 1187 | 181 | 0.12 | 0 |  | 1.224 |  | 521
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01220022.333/GR | 4.5 | 78.5 | 22 | 3.5 | 2081 | 317 | 0.21 | 0 |  | 1.206 |  | 908
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01220034.333/GR | 4.5 | 78.5 | 34 | 6.7 | 3180 | 485 | 0.32 | 0 |  | 1.452 |  | 1505
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01222011.333/GR | 4.5 | 86.5 | 11 | 2 | 1305 | 181 | 0.13 | 0 |  | 1.224 |  | 573
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01222022.333/GR | 4.5 | 86.5 | 22 | 3.5 | 2287 | 317 | 0.23 | 0 |  | 1.206 |  | 998
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01222034.333/GR | 4.5 | 86.5 | 34 | 6.7 | 3497 | 484 | 0.35 | 0 |  | 1.452 |  | 1655
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01224011.333/GR | 4.5 | 94.5 | 11 | 2 | 1424 | 181 | 0.14 | 0 |  | 1.224 |  | 625
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01224022.333/GR | 4.5 | 94.5 | 22 | 3.5 | 2496 | 317 | 0.25 | 0 |  | 1.206 |  | 1089
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01224034.333/GR | 4.5 | 94.5 | 34 | 6.7 | 3816 | 485 | 0.38 | 0 |  | 1.452 |  | 1806
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01226011.333/GR | 4.5 | 102.5 | 11 | 2 | 1542 | 181 | 0.15 | 0 |  | 1.224 |  | 677
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01226022.333/GR | 4.5 | 102.5 | 22 | 3.5 | 2704 | 317 | 0.27 | 0 |  | 1.206 |  | 1180
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01226034.333/GR | 4.5 | 102.5 | 34 | 6.7 | 4133 | 485 | 0.41 | 0 |  | 1.452 |  | 1956
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01228011.333/GR | 4.5 | 110 | 11 | 2 | 1661 | 181 | 0.17 | 0 |  | 1.224 |  | 729
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01228022.333/GR | 4.5 | 110 | 22 | 3.5 | 2913 | 317 | 0.29 | 0 |  | 1.206 |  | 1271
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01228034.333/GR | 4.5 | 110 | 34 | 6.7 | 4450 | 484 | 0.45 | 0 |  | 1.452 |  | 2106
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01230011.333/GR | 4.5 | 118 | 11 | 2 | 1782 | 181 | 0.18 | 0 |  | 1.224 |  | 782
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01230022.333/GR | 4.5 | 118 | 22 | 3.5 | 3119 | 317 | 0.31 | 0 |  | 1.206 |  | 1361
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01230034.333/GR | 4.5 | 118 | 34 | 6.7 | 4769 | 485 | 0.48 | 0 |  | 1.452 |  | 2257
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01232011.333/GR | 4.5 | 126 | 11 | 2 | 1900 | 181 | 0.19 | 0 |  | 1.224 |  | 834
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01232022.333/GR | 4.5 | 126 | 22 | 3.5 | 3328 | 317 | 0.33 | 0 |  | 1.206 |  | 1452
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01232034.333/GR | 4.5 | 126 | 34 | 6.7 | 5086 | 484 | 0.51 | 0 |  | 1.452 |  | 2407
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01234011.333/GR | 4.5 | 134 | 11 | 2 | 2018 | 181 | 0.2 | 0 |  | 1.224 |  | 886
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01234022.333/GR | 4.5 | 134 | 22 | 3.5 | 3536 | 317 | 0.35 | 0 |  | 1.206 |  | 1543
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01234034.333/GR | 4.5 | 134 | 34 | 6.7 | 5405 | 485 | 0.54 | 0 |  | 1.452 |  | 2558
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01236011.333/GR | 4.5 | 141.5 | 11 | 2 | 2137 | 181 | 0.21 | 0 |  | 1.224 |  | 938
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01236022.333/GR | 4.5 | 141.5 | 22 | 3.5 | 3745 | 317 | 0.37 | 0 |  | 1.206 |  | 1634
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01236034.333/GR | 4.5 | 141.5 | 34 | 6.7 | 5722 | 484 | 0.57 | 0 |  | 1.452 |  | 2708
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01238011.333/GR | 4.5 | 149.5 | 11 | 2 | 2255 | 181 | 0.23 | 0 |  | 1.224 |  | 990
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01238022.333/GR | 4.5 | 149.5 | 22 | 3.5 | 3951 | 317 | 0.4 | 0 |  | 1.206 |  | 1724
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01238034.333/GR | 4.5 | 149.5 | 34 | 6.7 | 6041 | 485 | 0.6 | 0 |  | 1.452 |  | 2859
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01242011.333/GR | 4.5 | 165.5 | 11 | 2 | 2492 | 181 | 0.25 | 0 |  | 1.224 |  | 1094
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01242022.333/GR | 4.5 | 165.5 | 22 | 3.5 | 4368 | 317 | 0.44 | 0 |  | 1.206 |  | 1906
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01242034.333/GR | 4.5 | 165.5 | 34 | 6.7 | 6677 | 485 | 0.67 | 0 |  | 1.452 |  | 3160
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01246011.333/GR | 4.5 | 181 | 11 | 2 | 2729 | 181 | 0.27 | 0 |  | 1.224 |  | 1198
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01246022.333/GR | 4.5 | 181 | 22 | 3.5 | 4783 | 317 | 0.48 | 0 |  | 1.206 |  | 2087
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01246034.333/GR | 4.5 | 181 | 34 | 6.7 | 7313 | 485 | 0.73 | 0 |  | 1.452 |  | 3461
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01810011.333/GR | 7 | 39.5 | 11 | 2 | 879 | 268 | 0.09 | 0 |  | 1.248 |  | 389
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01810022.333/GR | 7 | 39.5 | 22 | 3.5 | 1368 | 417 | 0.14 | 0 |  | 1.349 |  | 626
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01810034.333/GR | 7 | 39.5 | 34 | 6.7 | 2409 | 734 | 0.24 | 0 |  | 1.452 |  | 1140
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01812011.333/GR | 7 | 47 | 11 | 2 | 1053 | 267 | 0.11 | 0 |  | 1.248 |  | 466
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01812022.333/GR | 7 | 47 | 22 | 3.5 | 1642 | 417 | 0.16 | 0 |  | 1.349 |  | 751
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01812034.333/GR | 7 | 47 | 34 | 6.7 | 2893 | 735 | 0.29 | 0 |  | 1.452 |  | 1369
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01814011.333/GR | 7 | 55 | 11 | 2 | 1230 | 268 | 0.12 | 0 |  | 1.248 |  | 544
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01814022.333/GR | 7 | 55 | 22 | 3.5 | 1915 | 417 | 0.19 | 0 |  | 1.349 |  | 876
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01814034.333/GR | 7 | 55 | 34 | 6.7 | 3374 | 735 | 0.34 | 0 |  | 1.452 |  | 1597
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01816011.333/GR | 7 | 63 | 11 | 2 | 1406 | 268 | 0.14 | 0 |  | 1.248 |  | 622
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01816022.333/GR | 7 | 63 | 22 | 3.5 | 2188 | 417 | 0.22 | 0 |  | 1.349 |  | 1001
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01816034.333/GR | 7 | 63 | 34 | 6.7 | 3856 | 735 | 0.39 | 0 |  | 1.452 |  | 1825
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01818011.333/GR | 7 | 71 | 11 | 2 | 1580 | 268 | 0.16 | 0 |  | 1.248 |  | 699
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01818022.333/GR | 7 | 71 | 22 | 3.5 | 2462 | 417 | 0.25 | 0 |  | 1.349 |  | 1126
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01818034.333/GR | 7 | 71 | 34 | 6.7 | 4338 | 735 | 0.43 | 0 |  | 1.452 |  | 2053
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01820011.333/GR | 7 | 78.5 | 11 | 2 | 1756 | 268 | 0.18 | 0 |  | 1.248 |  | 777
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01820022.333/GR | 7 | 78.5 | 22 | 3.5 | 2737 | 417 | 0.27 | 0 |  | 1.349 |  | 1252
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01820034.333/GR | 7 | 78.5 | 34 | 6.7 | 4820 | 735 | 0.48 | 0 |  | 1.452 |  | 2281
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01822011.333/GR | 7 | 86.5 | 11 | 2 | 1932 | 268 | 0.19 | 0 |  | 1.248 |  | 855
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01822022.333/GR | 7 | 86.5 | 22 | 3.5 | 3010 | 417 | 0.3 | 0 |  | 1.349 |  | 1377
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01822034.333/GR | 7 | 86.5 | 34 | 6.7 | 5302 | 735 | 0.53 | 0 |  | 1.452 |  | 2509
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01824011.333/GR | 7 | 94.5 | 11 | 2 | 2106 | 267 | 0.21 | 0 |  | 1.248 |  | 932
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01824022.333/GR | 7 | 94.5 | 22 | 3.5 | 3283 | 417 | 0.33 | 0 |  | 1.349 |  | 1502
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01824034.333/GR | 7 | 94.5 | 34 | 6.7 | 5783 | 734 | 0.58 | 0 |  | 1.452 |  | 2737
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01826011.333/GR | 7 | 102.5 | 11 | 2 | 2283 | 268 | 0.23 | 0 |  | 1.248 |  | 1010
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01826022.333/GR | 7 | 102.5 | 22 | 3.5 | 3557 | 417 | 0.36 | 0 |  | 1.349 |  | 1627
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01826034.333/GR | 7 | 102.5 | 34 | 6.7 | 6265 | 734 | 0.63 | 0 |  | 1.452 |  | 2965
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01828011.333/GR | 7 | 110 | 11 | 2 | 2459 | 268 | 0.25 | 0 |  | 1.248 |  | 1088
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01828022.333/GR | 7 | 110 | 22 | 3.5 | 3830 | 417 | 0.38 | 0 |  | 1.349 |  | 1752
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01828034.333/GR | 7 | 110 | 34 | 6.7 | 6747 | 734 | 0.67 | 0 |  | 1.452 |  | 3193
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01830011.333/GR | 7 | 118 | 11 | 2 | 2635 | 268 | 0.26 | 0 |  | 1.248 |  | 1166
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01830022.333/GR | 7 | 118 | 22 | 3.5 | 4103 | 417 | 0.41 | 0 |  | 1.349 |  | 1877
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01830034.333/GR | 7 | 118 | 34 | 6.7 | 7229 | 734 | 0.72 | 0 |  | 1.452 |  | 3421
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01832011.333/GR | 7 | 126 | 11 | 2 | 2809 | 268 | 0.28 | 0 |  | 1.248 |  | 1243
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01832022.333/GR | 7 | 126 | 22 | 3.5 | 4377 | 417 | 0.44 | 0 |  | 1.349 |  | 2002
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01832034.333/GR | 7 | 126 | 34 | 6.7 | 7710 | 734 | 0.77 | 0 |  | 1.452 |  | 3649
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01834011.333/GR | 7 | 134 | 11 | 2 | 2986 | 268 | 0.3 | 0 |  | 1.248 |  | 1321
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01834022.333/GR | 7 | 134 | 22 | 3.5 | 4652 | 417 | 0.47 | 0 |  | 1.349 |  | 2128
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01834034.333/GR | 7 | 134 | 34 | 6.7 | 8192 | 734 | 0.82 | 0 |  | 1.452 |  | 3877
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01836011.333/GR | 7 | 141.5 | 11 | 2 | 3162 | 268 | 0.32 | 0 |  | 1.248 |  | 1399
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01836022.333/GR | 7 | 141.5 | 22 | 3.5 | 4925 | 417 | 0.49 | 0 |  | 1.349 |  | 2253
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01836034.333/GR | 7 | 141.5 | 34 | 6.7 | 8676 | 735 | 0.87 | 0 |  | 1.452 |  | 4106
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01838011.333/GR | 7 | 149.5 | 11 | 2 | 3336 | 268 | 0.33 | 0 |  | 1.248 |  | 1476
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01838022.333/GR | 7 | 149.5 | 22 | 3.5 | 5198 | 417 | 0.52 | 0 |  | 1.349 |  | 2378
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01838034.333/GR | 7 | 149.5 | 34 | 6.7 | 9158 | 735 | 0.92 | 0 |  | 1.452 |  | 4334
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01842011.333/GR | 7 | 165.5 | 11 | 2 | 3689 | 268 | 0.37 | 0 |  | 1.248 |  | 1632
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01842022.333/GR | 7 | 165.5 | 22 | 3.5 | 5745 | 417 | 0.57 | 0 |  | 1.349 |  | 2628
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01842034.333/GR | 7 | 165.5 | 34 | 6.7 | 10121 | 734 | 1.01 | 0 |  | 1.452 |  | 4790
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01846011.333/GR | 7 | 181 | 11 | 2 | 4039 | 268 | 0.4 | 0 |  | 1.248 |  | 1787
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01846022.333/GR | 7 | 181 | 22 | 3.5 | 6292 | 417 | 0.63 | 0 |  | 1.349 |  | 2878
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.01846034.333/GR | 7 | 181 | 34 | 6.7 | 11085 | 735 | 1.11 | 0 |  | 1.452 |  | 5246
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02406011.333/GR | 9.5 | 23.5 | 11 | 2 | 644 | 327 | 0.06 | 0 |  | 1.248 |  | 285
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02406022.333/GR | 9.5 | 23.5 | 22 | 3.5 | 1043 | 530 | 0.1 | 0 |  | 1.349 |  | 477
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02406034.333/GR | 9.5 | 23.5 | 34 | 6.7 | 1849 | 939 | 0.18 | 0 |  | 1.452 |  | 875
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02408011.333/GR | 9.5 | 31.5 | 11 | 2 | 859 | 327 | 0.09 | 0 |  | 1.248 |  | 380
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02408022.333/GR | 9.5 | 31.5 | 22 | 3.5 | 1390 | 530 | 0.14 | 0 |  | 1.349 |  | 636
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02408034.333/GR | 9.5 | 31.5 | 34 | 6.7 | 2464 | 939 | 0.25 | 0 |  | 1.452 |  | 1166
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02410011.333/GR | 9.5 | 39.5 | 11 | 2 | 1074 | 327 | 0.11 | 0 |  | 1.248 |  | 475
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02410022.333/GR | 9.5 | 39.5 | 22 | 3.5 | 1736 | 529 | 0.17 | 0 |  | 1.349 |  | 794
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02410034.333/GR | 9.5 | 39.5 | 34 | 6.7 | 3081 | 939 | 0.31 | 0 |  | 1.452 |  | 1458
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02412011.333/GR | 9.5 | 47 | 11 | 2 | 1288 | 327 | 0.13 | 0 |  | 1.248 |  | 570
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02412022.333/GR | 9.5 | 47 | 22 | 3.5 | 2083 | 529 | 0.21 | 0 |  | 1.349 |  | 953
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02412034.333/GR | 9.5 | 47 | 34 | 6.7 | 3696 | 939 | 0.37 | 0 |  | 1.452 |  | 1749
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02414011.333/GR | 9.5 | 55 | 11 | 2 | 1503 | 327 | 0.15 | 0 |  | 1.248 |  | 665
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02414022.333/GR | 9.5 | 55 | 22 | 3.5 | 2431 | 529 | 0.24 | 0 |  | 1.349 |  | 1112
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02414034.333/GR | 9.5 | 55 | 34 | 6.7 | 4313 | 939 | 0.43 | 0 |  | 1.452 |  | 2041
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02416011.333/GR | 9.5 | 63 | 11 | 2 | 1718 | 327 | 0.17 | 0 |  | 1.248 |  | 760
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02416022.333/GR | 9.5 | 63 | 22 | 3.5 | 2779 | 529 | 0.28 | 0 |  | 1.349 |  | 1271
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02416034.333/GR | 9.5 | 63 | 34 | 6.7 | 4928 | 939 | 0.49 | 0 |  | 1.452 |  | 2332
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02418011.333/GR | 9.5 | 71 | 11 | 2 | 1932 | 327 | 0.19 | 0 |  | 1.248 |  | 855
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02418022.333/GR | 9.5 | 71 | 22 | 3.5 | 3126 | 529 | 0.31 | 0 |  | 1.349 |  | 1430
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02418034.333/GR | 9.5 | 71 | 34 | 6.7 | 5545 | 939 | 0.55 | 0 |  | 1.452 |  | 2624
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02420011.333/GR | 9.5 | 78.5 | 11 | 2 | 2147 | 327 | 0.21 | 0 |  | 1.248 |  | 950
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02420022.333/GR | 9.5 | 78.5 | 22 | 3.5 | 3474 | 529 | 0.35 | 0 |  | 1.349 |  | 1589
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02420034.333/GR | 9.5 | 78.5 | 34 | 6.7 | 6159 | 939 | 0.62 | 0 |  | 1.452 |  | 2915
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02422011.333/GR | 9.5 | 86.5 | 11 | 2 | 2362 | 327 | 0.24 | 0 |  | 1.248 |  | 1045
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02422022.333/GR | 9.5 | 86.5 | 22 | 3.5 | 3821 | 529 | 0.38 | 0 |  | 1.349 |  | 1748
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02422034.333/GR | 9.5 | 86.5 | 34 | 6.7 | 6776 | 939 | 0.68 | 0 |  | 1.452 |  | 3207
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02424011.333/GR | 9.5 | 94.5 | 11 | 2 | 2577 | 327 | 0.26 | 0 |  | 1.248 |  | 1140
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02424022.333/GR | 9.5 | 94.5 | 22 | 3.5 | 4169 | 529 | 0.42 | 0 |  | 1.349 |  | 1907
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02424034.333/GR | 9.5 | 94.5 | 34 | 6.7 | 7391 | 939 | 0.74 | 0 |  | 1.452 |  | 3498
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02426011.333/GR | 9.5 | 102.5 | 11 | 2 | 2791 | 327 | 0.28 | 0 |  | 1.248 |  | 1235
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02426022.333/GR | 9.5 | 102.5 | 22 | 3.5 | 4514 | 529 | 0.45 | 0 |  | 1.349 |  | 2065
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02426034.333/GR | 9.5 | 102.5 | 34 | 6.7 | 8008 | 939 | 0.8 | 0 |  | 1.452 |  | 3790
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02428011.333/GR | 9.5 | 110 | 11 | 2 | 3006 | 327 | 0.3 | 0 |  | 1.248 |  | 1330
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02428022.333/GR | 9.5 | 110 | 22 | 3.5 | 4862 | 529 | 0.49 | 0 |  | 1.349 |  | 2224
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02428034.333/GR | 9.5 | 110 | 34 | 6.7 | 8623 | 939 | 0.86 | 0 |  | 1.452 |  | 4081
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02430011.333/GR | 9.5 | 118 | 11 | 2 | 3221 | 327 | 0.32 | 0 |  | 1.248 |  | 1425
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02430022.333/GR | 9.5 | 118 | 22 | 3.5 | 5209 | 529 | 0.52 | 0 |  | 1.349 |  | 2383
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.02430034.333/GR | 9.5 | 118 | 34 | 6.7 | 9240 | 939 | 0.92 | 0 |  | 1.452 |  | 4373
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03106011.333/GR | 12 | 23.5 | 11 | 2 | 755 | 384 | 0.08 | 0 |  | 1.248 |  | 334
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03106022.333/GR | 12 | 23.5 | 22 | 3.5 | 1248 | 634 | 0.12 | 0 |  | 1.349 |  | 571
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03106034.333/GR | 12 | 23.5 | 34 | 6.7 | 2152 | 1093 | 0.22 | 0 |  | 1.451 |  | 1018
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03108011.333/GR | 12 | 31.5 | 11 | 2 | 1006 | 383 | 0.1 | 0 |  | 1.248 |  | 445
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03108022.333/GR | 12 | 31.5 | 22 | 3.5 | 1664 | 634 | 0.17 | 0 |  | 1.349 |  | 761
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03108034.333/GR | 12 | 31.5 | 34 | 6.7 | 2868 | 1093 | 0.29 | 0 |  | 1.451 |  | 1357
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03110011.333/GR | 12 | 39.5 | 11 | 2 | 1257 | 383 | 0.13 | 0 |  | 1.248 |  | 556
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03110022.333/GR | 12 | 39.5 | 22 | 3.5 | 2079 | 634 | 0.21 | 0 |  | 1.349 |  | 951
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03110034.333/GR | 12 | 39.5 | 34 | 6.7 | 3587 | 1093 | 0.36 | 0 |  | 1.451 |  | 1697
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03112011.333/GR | 12 | 47 | 11 | 2 | 1510 | 384 | 0.15 | 0 |  | 1.248 |  | 668
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03112022.333/GR | 12 | 47 | 22 | 3.5 | 2496 | 634 | 0.25 | 0 |  | 1.349 |  | 1142
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03112034.333/GR | 12 | 47 | 34 | 6.7 | 4304 | 1093 | 0.43 | 0 |  | 1.451 |  | 2036
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03114011.333/GR | 12 | 55 | 11 | 2 | 1761 | 383 | 0.18 | 0 |  | 1.248 |  | 779
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03114022.333/GR | 12 | 55 | 22 | 3.5 | 2912 | 634 | 0.29 | 0 |  | 1.349 |  | 1332
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03114034.333/GR | 12 | 55 | 34 | 6.7 | 5020 | 1093 | 0.5 | 0 |  | 1.451 |  | 2375
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03116011.333/GR | 12 | 63 | 11 | 2 | 2012 | 383 | 0.2 | 0 |  | 1.248 |  | 890
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03116022.333/GR | 12 | 63 | 22 | 3.5 | 3327 | 634 | 0.33 | 0 |  | 1.349 |  | 1522
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03116034.333/GR | 12 | 63 | 34 | 6.7 | 5739 | 1093 | 0.57 | 0 |  | 1.451 |  | 2715
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03118011.333/GR | 12 | 71 | 11 | 2 | 2262 | 383 | 0.23 | 0 |  | 1.248 |  | 1001
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03118022.333/GR | 12 | 71 | 22 | 3.5 | 3745 | 634 | 0.37 | 0 |  | 1.349 |  | 1713
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03118034.333/GR | 12 | 71 | 34 | 6.7 | 6455 | 1093 | 0.65 | 0 |  | 1.451 |  | 3054
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03120011.333/GR | 12 | 78.5 | 11 | 2 | 2516 | 383 | 0.25 | 0 |  | 1.248 |  | 1113
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03120022.333/GR | 12 | 78.5 | 22 | 3.5 | 4160 | 634 | 0.42 | 0 |  | 1.349 |  | 1903
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03120034.333/GR | 12 | 78.5 | 34 | 6.7 | 7172 | 1093 | 0.72 | 0 |  | 1.451 |  | 3393
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03122011.333/GR | 12 | 86.5 | 11 | 2 | 2766 | 383 | 0.28 | 0 |  | 1.248 |  | 1224
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03122022.333/GR | 12 | 86.5 | 22 | 3.5 | 4575 | 634 | 0.46 | 0 |  | 1.349 |  | 2093
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03122034.333/GR | 12 | 86.5 | 34 | 6.7 | 7890 | 1093 | 0.79 | 0 |  | 1.451 |  | 3733
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03124011.333/GR | 12 | 94.5 | 11 | 2 | 3017 | 383 | 0.3 | 0 |  | 1.248 |  | 1335
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03124022.333/GR | 12 | 94.5 | 22 | 3.5 | 4991 | 634 | 0.5 | 0 |  | 1.349 |  | 2283
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03124034.333/GR | 12 | 94.5 | 34 | 6.7 | 8607 | 1093 | 0.86 | 0 |  | 1.451 |  | 4072
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03126011.333/GR | 12 | 102.5 | 11 | 2 | 3268 | 383 | 0.33 | 0 |  | 1.248 |  | 1446
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03126022.333/GR | 12 | 102.5 | 22 | 3.5 | 5408 | 634 | 0.54 | 0 |  | 1.349 |  | 2474
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03126034.333/GR | 12 | 102.5 | 34 | 6.7 | 9324 | 1093 | 0.93 | 0 |  | 1.451 |  | 4411
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03128011.333/GR | 12 | 110 | 11 | 2 | 3521 | 383 | 0.35 | 0 |  | 1.248 |  | 1558
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03128022.333/GR | 12 | 110 | 22 | 3.5 | 5824 | 634 | 0.58 | 0 |  | 1.349 |  | 2664
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03128034.333/GR | 12 | 110 | 34 | 6.7 | 10042 | 1093 | 1 | 0 |  | 1.451 |  | 4751
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03130011.333/GR | 12 | 118 | 11 | 2 | 3772 | 383 | 0.38 | 0 |  | 1.248 |  | 1669
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03130022.333/GR | 12 | 118 | 22 | 3.5 | 6239 | 634 | 0.62 | 0 |  | 1.349 |  | 2854
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03130034.333/GR | 12 | 118 | 34 | 6.7 | 10759 | 1093 | 1.08 | 0 |  | 1.451 |  | 5090
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03706011.333/GR | 14.5 | 23.5 | 11 | 2 | 859 | 436 | 0.09 | 0 |  | 1.248 |  | 380
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03706022.333/GR | 14.5 | 23.5 | 22 | 3.5 | 1441 | 732 | 0.14 | 0 |  | 1.349 |  | 659
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03708011.333/GR | 14.5 | 31.5 | 11 | 2 | 1146 | 437 | 0.11 | 0 |  | 1.248 |  | 507
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03708022.333/GR | 14.5 | 31.5 | 22 | 3.5 | 1922 | 732 | 0.19 | 0 |  | 1.349 |  | 879
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03710011.333/GR | 14.5 | 39.5 | 11 | 2 | 1431 | 436 | 0.14 | 0 |  | 1.248 |  | 633
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03710022.333/GR | 14.5 | 39.5 | 22 | 3.5 | 2400 | 732 | 0.24 | 0 |  | 1.349 |  | 1098
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03712011.333/GR | 14.5 | 47 | 11 | 2 | 1718 | 436 | 0.17 | 0 |  | 1.248 |  | 760
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03712022.333/GR | 14.5 | 47 | 22 | 3.5 | 2881 | 732 | 0.29 | 0 |  | 1.349 |  | 1318
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03714011.333/GR | 14.5 | 55 | 11 | 2 | 2005 | 437 | 0.2 | 0 |  | 1.248 |  | 887
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03714022.333/GR | 14.5 | 55 | 22 | 3.5 | 3362 | 732 | 0.34 | 0 |  | 1.349 |  | 1538
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03716011.333/GR | 14.5 | 63 | 11 | 2 | 2290 | 436 | 0.23 | 0 |  | 1.248 |  | 1013
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03716022.333/GR | 14.5 | 63 | 22 | 3.5 | 3841 | 732 | 0.38 | 0 |  | 1.349 |  | 1757
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03718011.333/GR | 14.5 | 71 | 11 | 2 | 2577 | 436 | 0.26 | 0 |  | 1.248 |  | 1140
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03718022.333/GR | 14.5 | 71 | 22 | 3.5 | 4322 | 732 | 0.43 | 0 |  | 1.349 |  | 1977
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03720011.333/GR | 14.5 | 78.5 | 11 | 2 | 2864 | 436 | 0.29 | 0 |  | 1.248 |  | 1267
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03720022.333/GR | 14.5 | 78.5 | 22 | 3.5 | 4803 | 732 | 0.48 | 0 |  | 1.349 |  | 2197
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03722011.333/GR | 14.5 | 86.5 | 11 | 2 | 3151 | 437 | 0.32 | 0 |  | 1.248 |  | 1394
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03722022.333/GR | 14.5 | 86.5 | 22 | 3.5 | 5282 | 732 | 0.53 | 0 |  | 1.349 |  | 2416
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03724011.333/GR | 14.5 | 94.5 | 11 | 2 | 3435 | 436 | 0.34 | 0 |  | 1.248 |  | 1520
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03724022.333/GR | 14.5 | 94.5 | 22 | 3.5 | 5762 | 732 | 0.58 | 0 |  | 1.349 |  | 2636
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03726011.333/GR | 14.5 | 102.5 | 11 | 2 | 3723 | 436 | 0.37 | 0 |  | 1.248 |  | 1647
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03726022.333/GR | 14.5 | 102.5 | 22 | 3.5 | 6243 | 732 | 0.62 | 0 |  | 1.349 |  | 2856
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03728011.333/GR | 14.5 | 110 | 11 | 2 | 4010 | 437 | 0.4 | 0 |  | 1.248 |  | 1774
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03728022.333/GR | 14.5 | 110 | 22 | 3.5 | 6722 | 732 | 0.67 | 0 |  | 1.349 |  | 3075
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03730011.333/GR | 14.5 | 118 | 11 | 2 | 4294 | 436 | 0.43 | 0 |  | 1.248 |  | 1900
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.03730022.333/GR | 14.5 | 118 | 22 | 3.5 | 7203 | 732 | 0.72 | 0 |  | 1.349 |  | 3295
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04306011.333/GR | 17 | 23.5 | 11 | 2 | 961 | 488 | 0.1 | 0 |  | 1.248 |  | 425
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04306022.333/GR | 17 | 23.5 | 22 | 3.5 | 1622 | 824 | 0.16 | 0 |  | 1.349 |  | 742
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04308011.333/GR | 17 | 31.5 | 11 | 2 | 1279 | 487 | 0.13 | 0 |  | 1.248 |  | 566
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04308022.333/GR | 17 | 31.5 | 22 | 3.5 | 2162 | 824 | 0.22 | 0 |  | 1.349 |  | 989
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04310011.333/GR | 17 | 39.5 | 11 | 2 | 1600 | 488 | 0.16 | 0 |  | 1.248 |  | 708
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04310022.333/GR | 17 | 39.5 | 22 | 3.5 | 2702 | 824 | 0.27 | 0 |  | 1.349 |  | 1236
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04312011.333/GR | 17 | 47 | 11 | 2 | 1919 | 487 | 0.19 | 0 |  | 1.248 |  | 849
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04312022.333/GR | 17 | 47 | 22 | 3.5 | 3242 | 823 | 0.32 | 0 |  | 1.349 |  | 1483
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04314011.333/GR | 17 | 55 | 11 | 2 | 2240 | 488 | 0.22 | 0 |  | 1.248 |  | 991
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04314022.333/GR | 17 | 55 | 22 | 3.5 | 3782 | 823 | 0.38 | 0 |  | 1.349 |  | 1730
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04316011.333/GR | 17 | 63 | 11 | 2 | 2559 | 487 | 0.26 | 0 |  | 1.248 |  | 1132
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04316022.333/GR | 17 | 63 | 22 | 3.5 | 4324 | 824 | 0.43 | 0 |  | 1.349 |  | 1978
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04318011.333/GR | 17 | 71 | 11 | 2 | 2879 | 488 | 0.29 | 0 |  | 1.248 |  | 1274
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04318022.333/GR | 17 | 71 | 22 | 3.5 | 4864 | 824 | 0.49 | 0 |  | 1.349 |  | 2225
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04320011.333/GR | 17 | 78.5 | 11 | 2 | 3198 | 487 | 0.32 | 0 |  | 1.248 |  | 1415
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04320022.333/GR | 17 | 78.5 | 22 | 3.5 | 5404 | 824 | 0.54 | 0 |  | 1.349 |  | 2472
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04322011.333/GR | 17 | 86.5 | 11 | 2 | 3519 | 488 | 0.35 | 0 |  | 1.248 |  | 1557
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04322022.333/GR | 17 | 86.5 | 22 | 3.5 | 5944 | 824 | 0.59 | 0 |  | 1.349 |  | 2719
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04324011.333/GR | 17 | 94.5 | 11 | 2 | 3838 | 487 | 0.38 | 0 |  | 1.248 |  | 1698
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04324022.333/GR | 17 | 94.5 | 22 | 3.5 | 6484 | 823 | 0.65 | 0 |  | 1.349 |  | 2966
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04326011.333/GR | 17 | 102.5 | 11 | 2 | 4159 | 488 | 0.42 | 0 |  | 1.248 |  | 1840
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04326022.333/GR | 17 | 102.5 | 22 | 3.5 | 7026 | 824 | 0.7 | 0 |  | 1.349 |  | 3214
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04328011.333/GR | 17 | 110 | 11 | 2 | 4477 | 487 | 0.45 | 0 |  | 1.248 |  | 1981
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04328022.333/GR | 17 | 110 | 22 | 3.5 | 7566 | 824 | 0.76 | 0 |  | 1.349 |  | 3461
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04330011.333/GR | 17 | 118 | 11 | 2 | 4798 | 487 | 0.48 | 0 |  | 1.248 |  | 2123
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.04330022.333/GR | 17 | 118 | 22 | 3.5 | 8106 | 824 | 0.81 | 0 |  | 1.349 |  | 3708
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05006011.333/GR | 19.5 | 23.5 | 11 | 2 | 1058 | 537 | 0.11 | 0 |  | 1.248 |  | 468
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05006022.333/GR | 19.5 | 23.5 | 22 | 3.5 | 1790 | 909 | 0.18 | 0 |  | 1.349 |  | 819
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05008011.333/GR | 19.5 | 31.5 | 11 | 2 | 1410 | 537 | 0.14 | 0 |  | 1.248 |  | 624
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05008022.333/GR | 19.5 | 31.5 | 22 | 3.5 | 2387 | 909 | 0.24 | 0 |  | 1.349 |  | 1092
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05010011.333/GR | 19.5 | 39.5 | 11 | 2 | 1763 | 537 | 0.18 | 0 |  | 1.248 |  | 780
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05010022.333/GR | 19.5 | 39.5 | 22 | 3.5 | 2984 | 910 | 0.3 | 0 |  | 1.349 |  | 1365
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05012011.333/GR | 19.5 | 47 | 11 | 2 | 2116 | 537 | 0.21 | 0 |  | 1.248 |  | 936
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05012022.333/GR | 19.5 | 47 | 22 | 3.5 | 3581 | 910 | 0.36 | 0 |  | 1.349 |  | 1638
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05014011.333/GR | 19.5 | 55 | 11 | 2 | 2466 | 537 | 0.25 | 0 |  | 1.248 |  | 1091
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05014022.333/GR | 19.5 | 55 | 22 | 3.5 | 4178 | 910 | 0.42 | 0 |  | 1.349 |  | 1911
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05016011.333/GR | 19.5 | 63 | 11 | 2 | 2818 | 537 | 0.28 | 0 |  | 1.248 |  | 1247
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05016022.333/GR | 19.5 | 63 | 22 | 3.5 | 4777 | 910 | 0.48 | 0 |  | 1.349 |  | 2185
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05018011.333/GR | 19.5 | 71 | 11 | 2 | 3171 | 537 | 0.32 | 0 |  | 1.248 |  | 1403
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05018022.333/GR | 19.5 | 71 | 22 | 3.5 | 5373 | 910 | 0.54 | 0 |  | 1.349 |  | 2458
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05020011.333/GR | 19.5 | 78.5 | 11 | 2 | 3524 | 537 | 0.35 | 0 |  | 1.248 |  | 1559
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05020022.333/GR | 19.5 | 78.5 | 22 | 3.5 | 5970 | 910 | 0.6 | 0 |  | 1.349 |  | 2731
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05022011.333/GR | 19.5 | 86.5 | 11 | 2 | 3876 | 537 | 0.39 | 0 |  | 1.248 |  | 1715
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05022022.333/GR | 19.5 | 86.5 | 22 | 3.5 | 6567 | 910 | 0.66 | 0 |  | 1.349 |  | 3004
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05024011.333/GR | 19.5 | 94.5 | 11 | 2 | 4229 | 537 | 0.42 | 0 |  | 1.248 |  | 1871
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05024022.333/GR | 19.5 | 94.5 | 22 | 3.5 | 7164 | 910 | 0.72 | 0 |  | 1.349 |  | 3277
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05026011.333/GR | 19.5 | 102.5 | 11 | 2 | 4581 | 537 | 0.46 | 0 |  | 1.248 |  | 2027
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05026022.333/GR | 19.5 | 102.5 | 22 | 3.5 | 7761 | 910 | 0.78 | 0 |  | 1.349 |  | 3550
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05028011.333/GR | 19.5 | 110 | 11 | 2 | 4934 | 537 | 0.49 | 0 |  | 1.248 |  | 2183
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05028022.333/GR | 19.5 | 110 | 22 | 3.5 | 8357 | 910 | 0.84 | 0 |  | 1.349 |  | 3823
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05030011.333/GR | 19.5 | 118 | 11 | 2 | 5287 | 537 | 0.53 | 0 |  | 1.248 |  | 2339
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05030022.333/GR | 19.5 | 118 | 22 | 3.5 | 8954 | 910 | 0.9 | 0 |  | 1.349 |  | 4096
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05606011.333/GR | 22 | 23.5 | 11 | 2 | 1153 | 586 | 0.12 | 0 |  | 1.248 |  | 510
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05606022.333/GR | 22 | 23.5 | 22 | 3.5 | 1950 | 991 | 0.2 | 0 |  | 1.349 |  | 892
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05608011.333/GR | 22 | 31.5 | 11 | 2 | 1537 | 586 | 0.15 | 0 |  | 1.248 |  | 680
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05608022.333/GR | 22 | 31.5 | 22 | 3.5 | 2601 | 991 | 0.26 | 0 |  | 1.349 |  | 1190
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05610011.333/GR | 22 | 39.5 | 11 | 2 | 1921 | 586 | 0.19 | 0 |  | 1.248 |  | 850
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05610022.333/GR | 22 | 39.5 | 22 | 3.5 | 3251 | 991 | 0.33 | 0 |  | 1.349 |  | 1487
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05612011.333/GR | 22 | 47 | 11 | 2 | 2305 | 585 | 0.23 | 0 |  | 1.248 |  | 1020
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05612022.333/GR | 22 | 47 | 22 | 3.5 | 3900 | 991 | 0.39 | 0 |  | 1.349 |  | 1784
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05614011.333/GR | 22 | 55 | 11 | 2 | 2690 | 586 | 0.27 | 0 |  | 1.248 |  | 1190
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05614022.333/GR | 22 | 55 | 22 | 3.5 | 4551 | 991 | 0.46 | 0 |  | 1.349 |  | 2082
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05616011.333/GR | 22 | 63 | 11 | 2 | 3074 | 586 | 0.31 | 0 |  | 1.248 |  | 1360
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05616022.333/GR | 22 | 63 | 22 | 3.5 | 5201 | 991 | 0.52 | 0 |  | 1.349 |  | 2379
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05618011.333/GR | 22 | 71 | 11 | 2 | 3458 | 586 | 0.35 | 0 |  | 1.248 |  | 1530
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05618022.333/GR | 22 | 71 | 22 | 3.5 | 5850 | 991 | 0.59 | 0 |  | 1.349 |  | 2676
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05620011.333/GR | 22 | 78.5 | 11 | 2 | 3842 | 586 | 0.38 | 0 |  | 1.248 |  | 1700
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05620022.333/GR | 22 | 78.5 | 22 | 3.5 | 6501 | 991 | 0.65 | 0 |  | 1.349 |  | 2974
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05622011.333/GR | 22 | 86.5 | 11 | 2 | 4227 | 586 | 0.42 | 0 |  | 1.248 |  | 1870
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05622022.333/GR | 22 | 86.5 | 22 | 3.5 | 7151 | 991 | 0.72 | 0 |  | 1.349 |  | 3271
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05624011.333/GR | 22 | 94.5 | 11 | 2 | 4611 | 586 | 0.46 | 0 |  | 1.248 |  | 2040
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05624022.333/GR | 22 | 94.5 | 22 | 3.5 | 7802 | 991 | 0.78 | 0 |  | 1.349 |  | 3569
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05626011.333/GR | 22 | 102.5 | 11 | 2 | 4995 | 586 | 0.5 | 0 |  | 1.248 |  | 2210
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05626022.333/GR | 22 | 102.5 | 22 | 3.5 | 8451 | 991 | 0.85 | 0 |  | 1.349 |  | 3866
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05628011.333/GR | 22 | 110 | 11 | 2 | 5379 | 586 | 0.54 | 0 |  | 1.248 |  | 2380
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05628022.333/GR | 22 | 110 | 22 | 3.5 | 9101 | 991 | 0.91 | 0 |  | 1.349 |  | 4163
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05630011.333/GR | 22 | 118 | 11 | 2 | 5761 | 585 | 0.58 | 0 |  | 1.248 |  | 2549
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.05630022.333/GR | 22 | 118 | 22 | 3.5 | 9752 | 991 | 0.98 | 0 |  | 1.349 |  | 4461
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06206011.333/GR | 24.5 | 23.5 | 11 | 2 | 1245 | 632 | 0.12 | 0 |  | 1.248 |  | 551
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06206022.333/GR | 24.5 | 23.5 | 22 | 3.5 | 2101 | 1067 | 0.21 | 0 |  | 1.349 |  | 961
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06208011.333/GR | 24.5 | 31.5 | 11 | 2 | 1661 | 633 | 0.17 | 0 |  | 1.248 |  | 735
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06208022.333/GR | 24.5 | 31.5 | 22 | 3.5 | 2800 | 1067 | 0.28 | 0 |  | 1.349 |  | 1281
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06210011.333/GR | 24.5 | 39.5 | 11 | 2 | 2077 | 633 | 0.21 | 0 |  | 1.248 |  | 919
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06210022.333/GR | 24.5 | 39.5 | 22 | 3.5 | 3500 | 1067 | 0.35 | 0 |  | 1.349 |  | 1601
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06212011.333/GR | 24.5 | 47 | 11 | 2 | 2491 | 633 | 0.25 | 0 |  | 1.248 |  | 1102
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06212022.333/GR | 24.5 | 47 | 22 | 3.5 | 4202 | 1067 | 0.42 | 0 |  | 1.349 |  | 1922
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06214011.333/GR | 24.5 | 55 | 11 | 2 | 2907 | 633 | 0.29 | 0 |  | 1.248 |  | 1286
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06214022.333/GR | 24.5 | 55 | 22 | 3.5 | 4901 | 1067 | 0.49 | 0 |  | 1.349 |  | 2242
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06216011.333/GR | 24.5 | 63 | 11 | 2 | 3322 | 633 | 0.33 | 0 |  | 1.248 |  | 1470
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06216022.333/GR | 24.5 | 63 | 22 | 3.5 | 5601 | 1067 | 0.56 | 0 |  | 1.349 |  | 2562
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06218011.333/GR | 24.5 | 71 | 11 | 2 | 3736 | 633 | 0.37 | 0 |  | 1.248 |  | 1653
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06218022.333/GR | 24.5 | 71 | 22 | 3.5 | 6300 | 1067 | 0.63 | 0 |  | 1.349 |  | 2882
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06220011.333/GR | 24.5 | 78.5 | 11 | 2 | 4152 | 633 | 0.42 | 0 |  | 1.248 |  | 1837
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06220022.333/GR | 24.5 | 78.5 | 22 | 3.5 | 7002 | 1067 | 0.7 | 0 |  | 1.349 |  | 3203
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06222011.333/GR | 24.5 | 86.5 | 11 | 2 | 4568 | 633 | 0.46 | 0 |  | 1.248 |  | 2021
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06222022.333/GR | 24.5 | 86.5 | 22 | 3.5 | 7702 | 1067 | 0.77 | 0 |  | 1.349 |  | 3523
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06224011.333/GR | 24.5 | 94.5 | 11 | 2 | 4984 | 633 | 0.5 | 0 |  | 1.248 |  | 2205
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06224022.333/GR | 24.5 | 94.5 | 22 | 3.5 | 8401 | 1067 | 0.84 | 0 |  | 1.349 |  | 3843
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06226011.333/GR | 24.5 | 102.5 | 11 | 2 | 5397 | 633 | 0.54 | 0 |  | 1.248 |  | 2388
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06226022.333/GR | 24.5 | 102.5 | 22 | 3.5 | 9101 | 1067 | 0.91 | 0 |  | 1.349 |  | 4163
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06228011.333/GR | 24.5 | 110 | 11 | 2 | 5813 | 633 | 0.58 | 0 |  | 1.248 |  | 2572
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06228022.333/GR | 24.5 | 110 | 22 | 3.5 | 9802 | 1067 | 0.98 | 0 |  | 1.349 |  | 4484
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06230011.333/GR | 24.5 | 118 | 11 | 2 | 6229 | 633 | 0.62 | 0 |  | 1.248 |  | 2756
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06230022.333/GR | 24.5 | 118 | 22 | 3.5 | 10502 | 1067 | 1.05 | 0 |  | 1.349 |  | 4804
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06906011.333/GR | 27 | 23.5 | 11 | 2 | 1338 | 680 | 0.13 | 0 |  | 1.249 |  | 592
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06906022.333/GR | 27 | 23.5 | 22 | 3.5 | 2241 | 1138 | 0.22 | 0 |  | 1.349 |  | 1025
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06908011.333/GR | 27 | 31.5 | 11 | 2 | 1783 | 679 | 0.18 | 0 |  | 1.249 |  | 789
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06908022.333/GR | 27 | 31.5 | 22 | 3.5 | 2988 | 1138 | 0.3 | 0 |  | 1.349 |  | 1367
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06910011.333/GR | 27 | 39.5 | 11 | 2 | 2228 | 679 | 0.22 | 0 |  | 1.249 |  | 986
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06910022.333/GR | 27 | 39.5 | 22 | 3.5 | 3736 | 1139 | 0.37 | 0 |  | 1.349 |  | 1709
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06912011.333/GR | 27 | 47 | 11 | 2 | 2673 | 679 | 0.27 | 0 |  | 1.249 |  | 1183
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06912022.333/GR | 27 | 47 | 22 | 3.5 | 4484 | 1139 | 0.45 | 0 |  | 1.349 |  | 2051
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06914011.333/GR | 27 | 55 | 11 | 2 | 3120 | 679 | 0.31 | 0 |  | 1.249 |  | 1381
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06914022.333/GR | 27 | 55 | 22 | 3.5 | 5229 | 1138 | 0.52 | 0 |  | 1.349 |  | 2392
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06916011.333/GR | 27 | 63 | 11 | 2 | 3565 | 679 | 0.36 | 0 |  | 1.249 |  | 1578
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06916022.333/GR | 27 | 63 | 22 | 3.5 | 5977 | 1139 | 0.6 | 0 |  | 1.349 |  | 2734
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06918011.333/GR | 27 | 71 | 11 | 2 | 4010 | 679 | 0.4 | 0 |  | 1.249 |  | 1775
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06918022.333/GR | 27 | 71 | 22 | 3.5 | 6724 | 1139 | 0.67 | 0 |  | 1.349 |  | 3076
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06920011.333/GR | 27 | 78.5 | 11 | 2 | 4456 | 679 | 0.45 | 0 |  | 1.249 |  | 1972
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06920022.333/GR | 27 | 78.5 | 22 | 3.5 | 7472 | 1139 | 0.75 | 0 |  | 1.349 |  | 3418
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06922011.333/GR | 27 | 86.5 | 11 | 2 | 4901 | 679 | 0.49 | 0 |  | 1.249 |  | 2169
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06922022.333/GR | 27 | 86.5 | 22 | 3.5 | 8220 | 1139 | 0.82 | 0 |  | 1.349 |  | 3760
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06924011.333/GR | 27 | 94.5 | 11 | 2 | 5348 | 679 | 0.53 | 0 |  | 1.249 |  | 2367
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06924022.333/GR | 27 | 94.5 | 22 | 3.5 | 8965 | 1139 | 0.9 | 0 |  | 1.349 |  | 4101
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06926011.333/GR | 27 | 102.5 | 11 | 2 | 5793 | 679 | 0.58 | 0 |  | 1.249 |  | 2564
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06926022.333/GR | 27 | 102.5 | 22 | 3.5 | 9713 | 1139 | 0.97 | 0 |  | 1.349 |  | 4443
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06928011.333/GR | 27 | 110 | 11 | 2 | 6238 | 679 | 0.62 | 0 |  | 1.249 |  | 2761
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06928022.333/GR | 27 | 110 | 22 | 3.5 | 10460 | 1139 | 1.05 | 0 |  | 1.349 |  | 4785
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06930011.333/GR | 27 | 118 | 11 | 2 | 6683 | 679 | 0.67 | 0 |  | 1.249 |  | 2958
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.06930022.333/GR | 27 | 118 | 22 | 3.5 | 11208 | 1139 | 1.12 | 0 |  | 1.349 |  | 5127
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07506011.333/GR | 29.5 | 23.5 | 11 | 2 | 1428 | 725 | 0.14 | 0 |  | 1.249 |  | 632
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07506022.333/GR | 29.5 | 23.5 | 22 | 3.5 | 2375 | 1207 | 0.24 | 0 |  | 1.348 |  | 1086
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07508011.333/GR | 29.5 | 31.5 | 11 | 2 | 1902 | 725 | 0.19 | 0 |  | 1.249 |  | 842
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07508022.333/GR | 29.5 | 31.5 | 22 | 3.5 | 3166 | 1206 | 0.32 | 0 |  | 1.348 |  | 1448
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07510011.333/GR | 29.5 | 39.5 | 11 | 2 | 2379 | 725 | 0.24 | 0 |  | 1.249 |  | 1053
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07510022.333/GR | 29.5 | 39.5 | 22 | 3.5 | 3958 | 1206 | 0.4 | 0 |  | 1.348 |  | 1810
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07512011.333/GR | 29.5 | 47 | 11 | 2 | 2854 | 725 | 0.29 | 0 |  | 1.249 |  | 1263
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07512022.333/GR | 29.5 | 47 | 22 | 3.5 | 4750 | 1207 | 0.48 | 0 |  | 1.348 |  | 2172
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07514011.333/GR | 29.5 | 55 | 11 | 2 | 3330 | 725 | 0.33 | 0 |  | 1.249 |  | 1474
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07514022.333/GR | 29.5 | 55 | 22 | 3.5 | 5541 | 1206 | 0.55 | 0 |  | 1.348 |  | 2534
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07516011.333/GR | 29.5 | 63 | 11 | 2 | 3805 | 725 | 0.38 | 0 |  | 1.249 |  | 1684
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07516022.333/GR | 29.5 | 63 | 22 | 3.5 | 6333 | 1206 | 0.63 | 0 |  | 1.348 |  | 2896
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07518011.333/GR | 29.5 | 71 | 11 | 2 | 4282 | 725 | 0.43 | 0 |  | 1.249 |  | 1895
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07518022.333/GR | 29.5 | 71 | 22 | 3.5 | 7125 | 1207 | 0.71 | 0 |  | 1.348 |  | 3258
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07520011.333/GR | 29.5 | 78.5 | 11 | 2 | 4756 | 725 | 0.48 | 0 |  | 1.249 |  | 2105
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07520022.333/GR | 29.5 | 78.5 | 22 | 3.5 | 7916 | 1206 | 0.79 | 0 |  | 1.348 |  | 3620
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07522011.333/GR | 29.5 | 86.5 | 11 | 2 | 5233 | 725 | 0.52 | 0 |  | 1.249 |  | 2316
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07522022.333/GR | 29.5 | 86.5 | 22 | 3.5 | 8708 | 1206 | 0.87 | 0 |  | 1.348 |  | 3982
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07524011.333/GR | 29.5 | 94.5 | 11 | 2 | 5707 | 725 | 0.57 | 0 |  | 1.249 |  | 2526
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07524022.333/GR | 29.5 | 94.5 | 22 | 3.5 | 9499 | 1206 | 0.95 | 0 |  | 1.348 |  | 4344
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07526011.333/GR | 29.5 | 102.5 | 11 | 2 | 6184 | 725 | 0.62 | 0 |  | 1.249 |  | 2737
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07526022.333/GR | 29.5 | 102.5 | 22 | 3.5 | 10291 | 1206 | 1.03 | 0 |  | 1.348 |  | 4706
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07528011.333/GR | 29.5 | 110 | 11 | 2 | 6661 | 725 | 0.67 | 0 |  | 1.249 |  | 2948
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07528022.333/GR | 29.5 | 110 | 22 | 3.5 | 11083 | 1206 | 1.11 | 0 |  | 1.348 |  | 5068
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07530011.333/GR | 29.5 | 118 | 11 | 2 | 7135 | 725 | 0.71 | 0 |  | 1.249 |  | 3158
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.07530022.333/GR | 29.5 | 118 | 22 | 3.5 | 11874 | 1206 | 1.19 | 0 |  | 1.348 |  | 5430
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08106011.333/GR | 32 | 23.5 | 11 | 2 | 1516 | 770 | 0.15 | 0 |  | 1.249 |  | 671
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08106022.333/GR | 32 | 23.5 | 22 | 3.5 | 2500 | 1270 | 0.25 | 0 |  | 1.348 |  | 1143
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08108011.333/GR | 32 | 31.5 | 11 | 2 | 2022 | 770 | 0.2 | 0 |  | 1.249 |  | 895
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08108022.333/GR | 32 | 31.5 | 22 | 3.5 | 3333 | 1270 | 0.33 | 0 |  | 1.348 |  | 1524
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08110011.333/GR | 32 | 39.5 | 11 | 2 | 2528 | 771 | 0.25 | 0 |  | 1.249 |  | 1119
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08110022.333/GR | 32 | 39.5 | 22 | 3.5 | 4166 | 1270 | 0.42 | 0 |  | 1.348 |  | 1905
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08112011.333/GR | 32 | 47 | 11 | 2 | 3032 | 770 | 0.3 | 0 |  | 1.249 |  | 1342
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08112022.333/GR | 32 | 47 | 22 | 3.5 | 4999 | 1270 | 0.5 | 0 |  | 1.348 |  | 2286
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08114011.333/GR | 32 | 55 | 11 | 2 | 3538 | 770 | 0.35 | 0 |  | 1.249 |  | 1566
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08114022.333/GR | 32 | 55 | 22 | 3.5 | 5832 | 1270 | 0.58 | 0 |  | 1.348 |  | 2667
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08116011.333/GR | 32 | 63 | 11 | 2 | 4044 | 770 | 0.4 | 0 |  | 1.249 |  | 1790
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08116022.333/GR | 32 | 63 | 22 | 3.5 | 6665 | 1270 | 0.67 | 0 |  | 1.348 |  | 3048
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08118011.333/GR | 32 | 71 | 11 | 2 | 4548 | 770 | 0.45 | 0 |  | 1.249 |  | 2013
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08118022.333/GR | 32 | 71 | 22 | 3.5 | 7501 | 1270 | 0.75 | 0 |  | 1.348 |  | 3430
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08120011.333/GR | 32 | 78.5 | 11 | 2 | 5054 | 770 | 0.51 | 0 |  | 1.249 |  | 2237
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08120022.333/GR | 32 | 78.5 | 22 | 3.5 | 8334 | 1270 | 0.83 | 0 |  | 1.348 |  | 3811
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08122011.333/GR | 32 | 86.5 | 11 | 2 | 5560 | 770 | 0.56 | 0 |  | 1.249 |  | 2461
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08122022.333/GR | 32 | 86.5 | 22 | 3.5 | 9167 | 1270 | 0.92 | 0 |  | 1.348 |  | 4192
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08124011.333/GR | 32 | 94.5 | 11 | 2 | 6064 | 770 | 0.61 | 0 |  | 1.249 |  | 2684
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08124022.333/GR | 32 | 94.5 | 22 | 3.5 | 10000 | 1270 | 1 | 0 |  | 1.348 |  | 4573
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08126011.333/GR | 32 | 102.5 | 11 | 2 | 6570 | 770 | 0.66 | 0 |  | 1.249 |  | 2908
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08126022.333/GR | 32 | 102.5 | 22 | 3.5 | 10833 | 1270 | 1.08 | 0 |  | 1.348 |  | 4954
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08128011.333/GR | 32 | 110 | 11 | 2 | 7077 | 770 | 0.71 | 0 |  | 1.249 |  | 3132
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08128022.333/GR | 32 | 110 | 22 | 3.5 | 11667 | 1270 | 1.17 | 0 |  | 1.348 |  | 5335
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08130011.333/GR | 32 | 118 | 11 | 2 | 7583 | 770 | 0.76 | 0 |  | 1.249 |  | 3356
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08130022.333/GR | 32 | 118 | 22 | 3.5 | 12500 | 1270 | 1.25 | 0 |  | 1.348 |  | 5716
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08706011.333/GR | 34.5 | 23.5 | 11 | 2 | 1604 | 815 | 0.16 | 0 |  | 1.249 |  | 710
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08706022.333/GR | 34.5 | 23.5 | 22 | 3.5 | 2618 | 1330 | 0.26 | 0 |  | 1.348 |  | 1197
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08708011.333/GR | 34.5 | 31.5 | 11 | 2 | 2140 | 815 | 0.21 | 0 |  | 1.249 |  | 947
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08708022.333/GR | 34.5 | 31.5 | 22 | 3.5 | 3490 | 1330 | 0.35 | 0 |  | 1.348 |  | 1596
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08710011.333/GR | 34.5 | 39.5 | 11 | 2 | 2675 | 815 | 0.27 | 0 |  | 1.249 |  | 1184
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08710022.333/GR | 34.5 | 39.5 | 22 | 3.5 | 4363 | 1330 | 0.44 | 0 |  | 1.348 |  | 1995
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08712011.333/GR | 34.5 | 47 | 11 | 2 | 3208 | 815 | 0.32 | 0 |  | 1.249 |  | 1420
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08712022.333/GR | 34.5 | 47 | 22 | 3.5 | 5235 | 1330 | 0.52 | 0 |  | 1.348 |  | 2394
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08714011.333/GR | 34.5 | 55 | 11 | 2 | 3744 | 815 | 0.37 | 0 |  | 1.249 |  | 1657
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08714022.333/GR | 34.5 | 55 | 22 | 3.5 | 6108 | 1330 | 0.61 | 0 |  | 1.348 |  | 2793
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08716011.333/GR | 34.5 | 63 | 11 | 2 | 4279 | 815 | 0.43 | 0 |  | 1.249 |  | 1894
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08716022.333/GR | 34.5 | 63 | 22 | 3.5 | 6980 | 1330 | 0.7 | 0 |  | 1.348 |  | 3192
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08718011.333/GR | 34.5 | 71 | 11 | 2 | 4815 | 815 | 0.48 | 0 |  | 1.249 |  | 2131
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08718022.333/GR | 34.5 | 71 | 22 | 3.5 | 7853 | 1330 | 0.79 | 0 |  | 1.348 |  | 3591
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08720011.333/GR | 34.5 | 78.5 | 11 | 2 | 5348 | 815 | 0.53 | 0 |  | 1.249 |  | 2367
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08720022.333/GR | 34.5 | 78.5 | 22 | 3.5 | 8725 | 1330 | 0.87 | 0 |  | 1.348 |  | 3990
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08722011.333/GR | 34.5 | 86.5 | 11 | 2 | 5884 | 815 | 0.59 | 0 |  | 1.249 |  | 2604
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08722022.333/GR | 34.5 | 86.5 | 22 | 3.5 | 9598 | 1330 | 0.96 | 0 |  | 1.348 |  | 4389
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08724011.333/GR | 34.5 | 94.5 | 11 | 2 | 6419 | 815 | 0.64 | 0 |  | 1.249 |  | 2841
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08724022.333/GR | 34.5 | 94.5 | 22 | 3.5 | 10470 | 1330 | 1.05 | 0 |  | 1.348 |  | 4788
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08726011.333/GR | 34.5 | 102.5 | 11 | 2 | 6952 | 815 | 0.7 | 0 |  | 1.249 |  | 3077
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08726022.333/GR | 34.5 | 102.5 | 22 | 3.5 | 11341 | 1330 | 1.13 | 0 |  | 1.348 |  | 5186
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08728011.333/GR | 34.5 | 110 | 11 | 2 | 7488 | 815 | 0.75 | 0 |  | 1.249 |  | 3314
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08728022.333/GR | 34.5 | 110 | 22 | 3.5 | 12213 | 1329 | 1.22 | 0 |  | 1.348 |  | 5585
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08730011.333/GR | 34.5 | 118 | 11 | 2 | 8023 | 815 | 0.8 | 0 |  | 1.249 |  | 3551
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.08730022.333/GR | 34.5 | 118 | 22 | 3.5 | 13086 | 1330 | 1.31 | 0 |  | 1.348 |  | 5984
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09406011.333/GR | 37 | 23.5 | 11 | 2 | 1692 | 860 | 0.17 | 0 |  | 1.249 |  | 749
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09406022.333/GR | 37 | 23.5 | 22 | 3.5 | 2727 | 1385 | 0.27 | 0 |  | 1.348 |  | 1247
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09408011.333/GR | 37 | 31.5 | 11 | 2 | 2257 | 860 | 0.23 | 0 |  | 1.249 |  | 999
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09408022.333/GR | 37 | 31.5 | 22 | 3.5 | 3637 | 1386 | 0.36 | 0 |  | 1.348 |  | 1663
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09410011.333/GR | 37 | 39.5 | 11 | 2 | 2820 | 860 | 0.28 | 0 |  | 1.249 |  | 1248
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09410022.333/GR | 37 | 39.5 | 22 | 3.5 | 4546 | 1386 | 0.45 | 0 |  | 1.348 |  | 2079
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09412011.333/GR | 37 | 47 | 11 | 2 | 3385 | 860 | 0.34 | 0 |  | 1.249 |  | 1498
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09412022.333/GR | 37 | 47 | 22 | 3.5 | 5456 | 1386 | 0.55 | 0 |  | 1.348 |  | 2495
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09414011.333/GR | 37 | 55 | 11 | 2 | 3949 | 860 | 0.39 | 0 |  | 1.249 |  | 1748
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09414022.333/GR | 37 | 55 | 22 | 3.5 | 6364 | 1386 | 0.64 | 0 |  | 1.348 |  | 2910
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09416011.333/GR | 37 | 63 | 11 | 2 | 4512 | 860 | 0.45 | 0 |  | 1.249 |  | 1997
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09416022.333/GR | 37 | 63 | 22 | 3.5 | 7273 | 1386 | 0.73 | 0 |  | 1.348 |  | 3326
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09418011.333/GR | 37 | 71 | 11 | 2 | 5077 | 860 | 0.51 | 0 |  | 1.249 |  | 2247
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09418022.333/GR | 37 | 71 | 22 | 3.5 | 8183 | 1386 | 0.82 | 0 |  | 1.348 |  | 3742
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09420011.333/GR | 37 | 78.5 | 11 | 2 | 5640 | 860 | 0.56 | 0 |  | 1.249 |  | 2496
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09420022.333/GR | 37 | 78.5 | 22 | 3.5 | 9093 | 1386 | 0.91 | 0 |  | 1.348 |  | 4158
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09422011.333/GR | 37 | 86.5 | 11 | 2 | 6204 | 860 | 0.62 | 0 |  | 1.249 |  | 2746
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09422022.333/GR | 37 | 86.5 | 22 | 3.5 | 10002 | 1386 | 1 | 0 |  | 1.348 |  | 4574
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09424011.333/GR | 37 | 94.5 | 11 | 2 | 6769 | 860 | 0.68 | 0 |  | 1.249 |  | 2996
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09424022.333/GR | 37 | 94.5 | 22 | 3.5 | 10910 | 1386 | 1.09 | 0 |  | 1.348 |  | 4989
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09426011.333/GR | 37 | 102.5 | 11 | 2 | 7332 | 860 | 0.73 | 0 |  | 1.249 |  | 3245
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09426022.333/GR | 37 | 102.5 | 22 | 3.5 | 11820 | 1386 | 1.18 | 0 |  | 1.348 |  | 5405
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09428011.333/GR | 37 | 110 | 11 | 2 | 7897 | 860 | 0.79 | 0 |  | 1.249 |  | 3495
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09428022.333/GR | 37 | 110 | 22 | 3.5 | 12729 | 1386 | 1.27 | 0 |  | 1.348 |  | 5821
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09430011.333/GR | 37 | 118 | 11 | 2 | 8462 | 860 | 0.85 | 0 |  | 1.249 |  | 3745
Horizontal Wall | Panel Plus Horizontal Wall | PPHW.09430022.333/GR | 37 | 118 | 22 | 3.5 | 13639 | 1386 | 1.36 | 0 |  | 1.348 |  | 6237
Vertical Wall | Panel Plus Vertical Wall | PPVW.18002411.333/MM | 71 | 9.5 | 11 | 2 | 1286 | 1633 | 0.13 | 0 |  | 1.326 |  | 584
Vertical Wall | Panel Plus Vertical Wall | PPVW.18003111.333/MM | 71 | 12 | 11 | 2 | 1608 | 1581 | 0.16 | 0 |  | 1.326 |  | 730
Vertical Wall | Panel Plus Vertical Wall | PPVW.18003711.333/MM | 71 | 14.5 | 11 | 2 | 1927 | 1587 | 0.19 | 0 |  | 1.326 |  | 875
Vertical Wall | Panel Plus Vertical Wall | PPVW.18004311.333/MM | 71 | 17 | 11 | 2 | 2249 | 1594 | 0.22 | 0 |  | 1.326 |  | 1021
Vertical Wall | Panel Plus Vertical Wall | PPVW.18005011.333/MM | 71 | 19.5 | 11 | 2 | 2571 | 1567 | 0.26 | 0 |  | 1.326 |  | 1167
Vertical Wall | Panel Plus Vertical Wall | PPVW.18005611.333/MM | 71 | 22 | 11 | 2 | 2892 | 1574 | 0.29 | 0 |  | 1.326 |  | 1313
Vertical Wall | Panel Plus Vertical Wall | PPVW.18006211.333/MM | 71 | 24.5 | 11 | 2 | 3214 | 1580 | 0.32 | 0 |  | 1.326 |  | 1459
Vertical Wall | Panel Plus Vertical Wall | PPVW.18006911.333/MM | 71 | 27 | 11 | 2 | 3535 | 1562 | 0.35 | 0 |  | 1.326 |  | 1605
Vertical Wall | Panel Plus Vertical Wall | PPVW.18007511.333/MM | 71 | 29.5 | 11 | 2 | 3857 | 1567 | 0.39 | 0 |  | 1.326 |  | 1751
Vertical Wall | Panel Plus Vertical Wall | PPVW.18008111.333/MM | 71 | 32 | 11 | 2 | 4179 | 1573 | 0.42 | 0 |  | 1.326 |  | 1897
Vertical Wall | Panel Plus Vertical Wall | PPVW.18008711.333/MM | 71 | 34.5 | 11 | 2 | 4500 | 1577 | 0.45 | 0 |  | 1.326 |  | 2043
Vertical Wall | Panel Plus Vertical Wall | PPVW.18009411.333/MM | 71 | 37 | 11 | 2 | 4822 | 1564 | 0.48 | 0 |  | 1.326 |  | 2189
Vertical Wall | Panel Plus Vertical Wall | PPVW.20002411.333/MM | 78.5 | 9.5 | 11 | 2 | 1423 | 1807 | 0.14 | 0 |  | 1.316 |  | 644
Vertical Wall | Panel Plus Vertical Wall | PPVW.20003111.333/MM | 78.5 | 12 | 11 | 2 | 1779 | 1749 | 0.18 | 0 |  | 1.316 |  | 805
Vertical Wall | Panel Plus Vertical Wall | PPVW.20003711.333/MM | 78.5 | 14.5 | 11 | 2 | 2133 | 1757 | 0.21 | 0 |  | 1.316 |  | 965
Vertical Wall | Panel Plus Vertical Wall | PPVW.20004311.333/MM | 78.5 | 17 | 11 | 2 | 2488 | 1764 | 0.25 | 0 |  | 1.316 |  | 1126
Vertical Wall | Panel Plus Vertical Wall | PPVW.20005011.333/MM | 78.5 | 19.5 | 11 | 2 | 2844 | 1734 | 0.28 | 0 |  | 1.316 |  | 1287
Vertical Wall | Panel Plus Vertical Wall | PPVW.20005611.333/MM | 78.5 | 22 | 11 | 2 | 3200 | 1742 | 0.32 | 0 |  | 1.316 |  | 1448
Vertical Wall | Panel Plus Vertical Wall | PPVW.20006211.333/MM | 78.5 | 24.5 | 11 | 2 | 3556 | 1748 | 0.36 | 0 |  | 1.316 |  | 1609
Vertical Wall | Panel Plus Vertical Wall | PPVW.20006911.333/MM | 78.5 | 27 | 11 | 2 | 3912 | 1728 | 0.39 | 0 |  | 1.316 |  | 1770
Vertical Wall | Panel Plus Vertical Wall | PPVW.20007511.333/MM | 78.5 | 29.5 | 11 | 2 | 4268 | 1735 | 0.43 | 0 |  | 1.316 |  | 1931
Vertical Wall | Panel Plus Vertical Wall | PPVW.20008111.333/MM | 78.5 | 32 | 11 | 2 | 4623 | 1740 | 0.46 | 0 |  | 1.316 |  | 2092
Vertical Wall | Panel Plus Vertical Wall | PPVW.20008711.333/MM | 78.5 | 34.5 | 11 | 2 | 4979 | 1744 | 0.5 | 0 |  | 1.316 |  | 2253
Vertical Wall | Panel Plus Vertical Wall | PPVW.20009411.333/MM | 78.5 | 37 | 11 | 2 | 5335 | 1730 | 0.53 | 0 |  | 1.316 |  | 2414
Vertical Wall | Panel Plus Vertical Wall | PPVW.22002411.333/MM | 86.5 | 9.5 | 11 | 2 | 1552 | 1971 | 0.16 | 0 |  | 1.306 |  | 700
Vertical Wall | Panel Plus Vertical Wall | PPVW.22003111.333/MM | 86.5 | 12 | 11 | 2 | 1942 | 1909 | 0.19 | 0 |  | 1.306 |  | 876
Vertical Wall | Panel Plus Vertical Wall | PPVW.22003711.333/MM | 86.5 | 14.5 | 11 | 2 | 2330 | 1919 | 0.23 | 0 |  | 1.306 |  | 1051
Vertical Wall | Panel Plus Vertical Wall | PPVW.22004311.333/MM | 86.5 | 17 | 11 | 2 | 2718 | 1927 | 0.27 | 0 |  | 1.306 |  | 1226
Vertical Wall | Panel Plus Vertical Wall | PPVW.22005011.333/MM | 86.5 | 19.5 | 11 | 2 | 3106 | 1893 | 0.31 | 0 |  | 1.306 |  | 1401
Vertical Wall | Panel Plus Vertical Wall | PPVW.22005611.333/MM | 86.5 | 22 | 11 | 2 | 3494 | 1902 | 0.35 | 0 |  | 1.306 |  | 1576
Vertical Wall | Panel Plus Vertical Wall | PPVW.22006211.333/MM | 86.5 | 24.5 | 11 | 2 | 3883 | 1909 | 0.39 | 0 |  | 1.306 |  | 1751
Vertical Wall | Panel Plus Vertical Wall | PPVW.22006911.333/MM | 86.5 | 27 | 11 | 2 | 4271 | 1887 | 0.43 | 0 |  | 1.306 |  | 1926
Vertical Wall | Panel Plus Vertical Wall | PPVW.22007511.333/MM | 86.5 | 29.5 | 11 | 2 | 4659 | 1893 | 0.47 | 0 |  | 1.306 |  | 2101
Vertical Wall | Panel Plus Vertical Wall | PPVW.22008111.333/MM | 86.5 | 32 | 11 | 2 | 5047 | 1899 | 0.5 | 0 |  | 1.306 |  | 2276
Vertical Wall | Panel Plus Vertical Wall | PPVW.22008711.333/MM | 86.5 | 34.5 | 11 | 2 | 5435 | 1904 | 0.54 | 0 |  | 1.306 |  | 2451
Vertical Wall | Panel Plus Vertical Wall | PPVW.22009411.333/MM | 86.5 | 37 | 11 | 2 | 5825 | 1889 | 0.58 | 0 |  | 1.306 |  | 2627
Vertical Wall | Panel Plus Vertical Wall | PPVW.24002411.333/MM | 94.5 | 9.5 | 11 | 2 | 1677 | 2130 | 0.17 | 0 |  | 1.297 |  | 754
Vertical Wall | Panel Plus Vertical Wall | PPVW.24003111.333/MM | 94.5 | 12 | 11 | 2 | 2097 | 2062 | 0.21 | 0 |  | 1.297 |  | 943
Vertical Wall | Panel Plus Vertical Wall | PPVW.24003711.333/MM | 94.5 | 14.5 | 11 | 2 | 2515 | 2072 | 0.25 | 0 |  | 1.297 |  | 1131
Vertical Wall | Panel Plus Vertical Wall | PPVW.24004311.333/MM | 94.5 | 17 | 11 | 2 | 2936 | 2081 | 0.29 | 0 |  | 1.297 |  | 1320
Vertical Wall | Panel Plus Vertical Wall | PPVW.24005011.333/MM | 94.5 | 19.5 | 11 | 2 | 3354 | 2045 | 0.34 | 0 |  | 1.297 |  | 1508
Vertical Wall | Panel Plus Vertical Wall | PPVW.24005611.333/MM | 94.5 | 22 | 11 | 2 | 3774 | 2054 | 0.38 | 0 |  | 1.297 |  | 1697
Vertical Wall | Panel Plus Vertical Wall | PPVW.24006211.333/MM | 94.5 | 24.5 | 11 | 2 | 4192 | 2061 | 0.42 | 0 |  | 1.297 |  | 1885
Vertical Wall | Panel Plus Vertical Wall | PPVW.24006911.333/MM | 94.5 | 27 | 11 | 2 | 4612 | 2037 | 0.46 | 0 |  | 1.297 |  | 2074
Vertical Wall | Panel Plus Vertical Wall | PPVW.24007511.333/MM | 94.5 | 29.5 | 11 | 2 | 5031 | 2045 | 0.5 | 0 |  | 1.297 |  | 2262
Vertical Wall | Panel Plus Vertical Wall | PPVW.24008111.333/MM | 94.5 | 32 | 11 | 2 | 5451 | 2051 | 0.55 | 0 |  | 1.297 |  | 2451
Vertical Wall | Panel Plus Vertical Wall | PPVW.24008711.333/MM | 94.5 | 34.5 | 11 | 2 | 5869 | 2056 | 0.59 | 0 |  | 1.297 |  | 2639
Vertical Wall | Panel Plus Vertical Wall | PPVW.24009411.333/MM | 94.5 | 37 | 11 | 2 | 6289 | 2039 | 0.63 | 0 |  | 1.297 |  | 2828
Vertical Wall | Panel Plus Vertical Wall | PPVW.26002411.333/MM | 102.5 | 9.5 | 11 | 2 | 1796 | 2281 | 0.18 | 0 |  | 1.287 |  | 805
Vertical Wall | Panel Plus Vertical Wall | PPVW.26003111.333/MM | 102.5 | 12 | 11 | 2 | 2245 | 2207 | 0.22 | 0 |  | 1.287 |  | 1006
Vertical Wall | Panel Plus Vertical Wall | PPVW.26003711.333/MM | 102.5 | 14.5 | 11 | 2 | 2693 | 2218 | 0.27 | 0 |  | 1.287 |  | 1207
Vertical Wall | Panel Plus Vertical Wall | PPVW.26004311.333/MM | 102.5 | 17 | 11 | 2 | 3142 | 2227 | 0.31 | 0 |  | 1.287 |  | 1408
Vertical Wall | Panel Plus Vertical Wall | PPVW.26005011.333/MM | 102.5 | 19.5 | 11 | 2 | 3592 | 2190 | 0.36 | 0 |  | 1.287 |  | 1610
Vertical Wall | Panel Plus Vertical Wall | PPVW.26005611.333/MM | 102.5 | 22 | 11 | 2 | 4041 | 2199 | 0.4 | 0 |  | 1.287 |  | 1811
Vertical Wall | Panel Plus Vertical Wall | PPVW.26006211.333/MM | 102.5 | 24.5 | 11 | 2 | 4489 | 2207 | 0.45 | 0 |  | 1.287 |  | 2012
Vertical Wall | Panel Plus Vertical Wall | PPVW.26006911.333/MM | 102.5 | 27 | 11 | 2 | 4938 | 2181 | 0.49 | 0 |  | 1.287 |  | 2213
Vertical Wall | Panel Plus Vertical Wall | PPVW.26007511.333/MM | 102.5 | 29.5 | 11 | 2 | 5386 | 2189 | 0.54 | 0 |  | 1.287 |  | 2414
Vertical Wall | Panel Plus Vertical Wall | PPVW.26008111.333/MM | 102.5 | 32 | 11 | 2 | 5837 | 2196 | 0.58 | 0 |  | 1.287 |  | 2616
Vertical Wall | Panel Plus Vertical Wall | PPVW.26008711.333/MM | 102.5 | 34.5 | 11 | 2 | 6285 | 2202 | 0.63 | 0 |  | 1.287 |  | 2817
Vertical Wall | Panel Plus Vertical Wall | PPVW.26009411.333/MM | 102.5 | 37 | 11 | 2 | 6734 | 2184 | 0.67 | 0 |  | 1.287 |  | 3018
Vertical Wall | Panel Plus Vertical Wall | PPVW.28002411.333/MM | 110 | 9.5 | 11 | 2 | 1907 | 2422 | 0.19 | 0 |  | 1.277 |  | 852
Vertical Wall | Panel Plus Vertical Wall | PPVW.28003111.333/MM | 110 | 12 | 11 | 2 | 2386 | 2346 | 0.24 | 0 |  | 1.277 |  | 1066
Vertical Wall | Panel Plus Vertical Wall | PPVW.28003711.333/MM | 110 | 14.5 | 11 | 2 | 2863 | 2358 | 0.29 | 0 |  | 1.277 |  | 1279
Vertical Wall | Panel Plus Vertical Wall | PPVW.28004311.333/MM | 110 | 17 | 11 | 2 | 3340 | 2368 | 0.33 | 0 |  | 1.277 |  | 1492
Vertical Wall | Panel Plus Vertical Wall | PPVW.28005011.333/MM | 110 | 19.5 | 11 | 2 | 3817 | 2327 | 0.38 | 0 |  | 1.277 |  | 1705
Vertical Wall | Panel Plus Vertical Wall | PPVW.28005611.333/MM | 110 | 22 | 11 | 2 | 4294 | 2337 | 0.43 | 0 |  | 1.277 |  | 1918
Vertical Wall | Panel Plus Vertical Wall | PPVW.28006211.333/MM | 110 | 24.5 | 11 | 2 | 4771 | 2345 | 0.48 | 0 |  | 1.277 |  | 2131
Vertical Wall | Panel Plus Vertical Wall | PPVW.28006911.333/MM | 110 | 27 | 11 | 2 | 5247 | 2318 | 0.52 | 0 |  | 1.277 |  | 2344
Vertical Wall | Panel Plus Vertical Wall | PPVW.28007511.333/MM | 110 | 29.5 | 11 | 2 | 5724 | 2326 | 0.57 | 0 |  | 1.277 |  | 2557
Vertical Wall | Panel Plus Vertical Wall | PPVW.28008111.333/MM | 110 | 32 | 11 | 2 | 6201 | 2333 | 0.62 | 0 |  | 1.277 |  | 2770
Vertical Wall | Panel Plus Vertical Wall | PPVW.28008711.333/MM | 110 | 34.5 | 11 | 2 | 6678 | 2340 | 0.67 | 0 |  | 1.277 |  | 2983
Vertical Wall | Panel Plus Vertical Wall | PPVW.28009411.333/MM | 110 | 37 | 11 | 2 | 7157 | 2321 | 0.72 | 0 |  | 1.277 |  | 3197
Vertical Wall | Panel Plus Vertical Wall | PPVW.30002411.333/MM | 118 | 9.5 | 11 | 2 | 2015 | 2559 | 0.2 | 0 |  | 1.267 |  | 897
Vertical Wall | Panel Plus Vertical Wall | PPVW.30003111.333/MM | 118 | 12 | 11 | 2 | 2518 | 2476 | 0.25 | 0 |  | 1.267 |  | 1121
Vertical Wall | Panel Plus Vertical Wall | PPVW.30003711.333/MM | 118 | 14.5 | 11 | 2 | 3021 | 2489 | 0.3 | 0 |  | 1.267 |  | 1345
Vertical Wall | Panel Plus Vertical Wall | PPVW.30004311.333/MM | 118 | 17 | 11 | 2 | 3524 | 2498 | 0.35 | 0 |  | 1.267 |  | 1569
Vertical Wall | Panel Plus Vertical Wall | PPVW.30005011.333/MM | 118 | 19.5 | 11 | 2 | 4029 | 2456 | 0.4 | 0 |  | 1.267 |  | 1794
Vertical Wall | Panel Plus Vertical Wall | PPVW.30005611.333/MM | 118 | 22 | 11 | 2 | 4533 | 2467 | 0.45 | 0 |  | 1.267 |  | 2018
Vertical Wall | Panel Plus Vertical Wall | PPVW.30006211.333/MM | 118 | 24.5 | 11 | 2 | 5036 | 2476 | 0.5 | 0 |  | 1.267 |  | 2242
Vertical Wall | Panel Plus Vertical Wall | PPVW.30006911.333/MM | 118 | 27 | 11 | 2 | 5539 | 2447 | 0.55 | 0 |  | 1.267 |  | 2466
Vertical Wall | Panel Plus Vertical Wall | PPVW.30007511.333/MM | 118 | 29.5 | 11 | 2 | 6042 | 2455 | 0.6 | 0 |  | 1.267 |  | 2690
Vertical Wall | Panel Plus Vertical Wall | PPVW.30008111.333/MM | 118 | 32 | 11 | 2 | 6547 | 2464 | 0.65 | 0 |  | 1.267 |  | 2915
Vertical Wall | Panel Plus Vertical Wall | PPVW.30008711.333/MM | 118 | 34.5 | 11 | 2 | 7050 | 2470 | 0.71 | 0 |  | 1.267 |  | 3139
Vertical Wall | Panel Plus Vertical Wall | PPVW.30009411.333/MM | 118 | 37 | 11 | 2 | 7553 | 2449 | 0.76 | 0 |  | 1.267 |  | 3363

## Briza12
Selection Model 2022-10 | [47 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF |  |  |  | Entering T | 45 | EWT ºF | [5 empty] | 60 | 7.2222 | [25 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF |  |  |  | Return T | 55 | LWT ºF | [5 empty] | 48.8889 | 12.7778 | p_atm |  | h(mm) | 0 | [21 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF |  |  |  | Air T | 75 | AT ºF | [5 empty] | 18.3333 | 23.8889 | 101325 |  | cf_h | 1 | [21 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF |  |  |  | Mean T | 50 | ºF | [6 empty] | -13.7017 | -9.9666 | [25 empty] | -10
[13 empty] | Rel Humid | 50%
[7 empty] | Fanspeed | 100% |  |  |  |  | Fanspeed | 100% |  |  |  |  | *Sound pressure with an assumed room damping of 8dB(A) | [29 empty] | sensible cooling kengetallen
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º | [5 empty] | 45/55/75º (50% RH) | [6 empty] | N-Waarde |  | Heating kengetallen 75/65/20ºC | [5 empty] | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  | 16/18/27ºC | [5 empty] | Pessure Drop
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | Sensible Cooling in BTU/h | Total Cooling in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | H en C | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | a | b | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | a | b | Kolom | SalesGroup | JagaSourceCode Stnd
Horizontal Wall | Briza | BZMW.04107512 | 16.1 | 29.5 | 2pipe | 5.5 | 4094.7646 | 0.41 | 126 | 13 | 0.085827 | 0 | 1004.2217 | 1133.3016 | 0.23 | 126 | 13 | 0.029698 | 0 | 1 |  | 784.0931 | 57.9733 | 0.1949 | 0.21174 | 0.0074264 |  | 214 | 178 | 141 | 101 | 64 | [7 empty] | 13 | 7.2 | 4.3 | 2.6 | 1.6 |  | 6.2277e-05 | 1.8358 |  | 102.0759 | 4.9047 | 0.93056 | -0.0301 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZMW0.04107500
Horizontal Wall | Briza | BZMW.04109512 | 16.1 | 37.4 | 2pipe | 5.5 | 6743.7123 | 0.67 | 203.6 | 18 | 0.27226 | 0 | 1652.9378 | 1865.402 | 0.37 | 203.6 | 18 | 0.092681 | 0 | 1 |  | 237.1457 | 1211.6861 | -360.6249 | 44.4855 | -1.8028 |  | 346 | 287 | 223 | 172 | 108 | [7 empty] | 18 | 11.5 | 7.2 | 4.3 | 2.5 |  | 8.9126e-05 | 1.8148 |  | 173.5639 | 6.8789 | 0.95253 | 0.014766 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZMW0.04109500
Horizontal Wall | Briza | BZMW.04112512 | 16.1 | 49.2 | 2pipe | 5.5 | 10711.4204 | 1.07 | 263.7 | 24 | 0.85962 | 0 | 2620.9816 | 2957.8755 | 0.59 | 263.7 | 24 | 0.29187 | 0 | 1 |  | 2161.5461 | 142.0685 | -6.6767 | 1.4786 | -0.0026387 |  | 448 | 381 | 298 | 221 | 146 | [7 empty] | 24 | 14 | 8 | 4.8 | 2.6 |  | 0.00012049 | 1.8146 |  | 290.7155 | 9.4024 | 0.7828 | 0.095719 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZMW0.04112500
Horizontal Wall | Briza | BZMW.04114512 | 16.1 | 57.1 | 2pipe | 5.5 | 13353.2454 | 1.33 | 300.2 | 28.8 | 1.4897 | 0 | 3272.0821 | 3692.6668 | 0.74 | 300.2 | 28.8 | 0.5097 | 0 | 1 |  | 2614.5642 | 199.5924 | -6.7862 | 1.5119 | 0 |  | 510 | 466 | 373 | 268 | 173 | [7 empty] | 28.8 | 18.5 | 10.3 | 5.5 | 2.8 |  | 0.00012933 | 1.8293 |  | 379.7621 | 15.6645 | -0.25189 | 0.18632 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZMW0.04114500
Horizontal Wall | Briza | BZMW.05507512 | 21.7 | 29.5 | 2pipe | 5.5 | 6349.1031 | 0.63 | 134.2 | 16.8 | 0.36033 | 0 | 1558.3339 | 1758.638 | 0.35 | 134.2 | 16.8 | 0.12409 | 0 | 1 |  | 1095.2129 | 152.8798 | -0.35664 | 0 | 0 |  | 228 | 193 | 154 | 118 | 81 | [7 empty] | 16.8 | 9.6 | 5.5 | 3.2 | 2 |  | 0.00013264 | 1.8137 |  | 124.6876 | 22.688 | -0.072116 | -0.002007 | -0.0010144 |  | 0.00013264 | 1.8137 |  | D04 | BZMW0.05507500
Horizontal Wall | Briza | BZMW.05509512 | 21.7 | 37.4 | 2pipe | 5.5 | 10510.3157 | 1.05 | 195.4 | 15.6 | 1.1948 | 0 | 2580.9092 | 2912.6524 | 0.58 | 195.4 | 15.6 | 0.40549 | 0 | 1 |  | 1733.6903 | 251.4329 | 4.0609 | -0.36935 | 0 |  | 332 | 291 | 238 | 176 | 116 | [7 empty] | 15.6 | 9.6 | 5.7 | 3.6 | 2.2 |  | 0.00016748 | 1.8208 |  | 244.8221 | 20.927 | 2.4216 | -0.14606 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZMW0.05509500
Horizontal Wall | Briza | BZMW.05512512 | 21.7 | 49.2 | 2pipe | 5.5 | 16755.1906 | 1.67 | 274.9 | 28.8 | 3.7281 | 0 | 4113.8381 | 4642.6199 | 0.93 | 274.9 | 28.8 | 1.2906 | 0 | 1 |  | 2743.7411 | 390.8208 | 10.6017 | -0.88151 | 0 |  | 467 | 398 | 321 | 236 | 153 | [7 empty] | 28.8 | 18 | 10 | 5.4 | 2.8 |  | 0.00023644 | 1.8121 |  | 404.4386 | 26.677 | 4.6735 | -0.26157 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZMW0.05512500
Horizontal Wall | Briza | BZMW.05514512 | 21.7 | 57.1 | 2pipe | 5.5 | 20913.2128 | 2.09 | 312.5 | 28.8 | 6.5675 | 0 | 5138.0931 | 5798.5298 | 1.16 | 312.5 | 28.8 | 2.2553 | 0 | 1 |  | 3621.1756 | 398.101 | 26.2681 | -1.7033 | 0 |  | 531 | 455 | 360 | 270 | 182 | [7 empty] | 28.8 | 18 | 10 | 5.5 | 2.8 |  | 0.0002717 | 1.8154 |  | 500.4299 | 34.9711 | 5.5713 | -0.31193 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZMW0.05514500
Horizontal Wall | Briza | BZMW.04107512/4 | 16.1 | 29.5 | 4pipe | 5.5 | 3277.2674 | 0.33 | 84.2 | 13.7 | 0.057618 | 0 | 801.1687 | 904.1487 | 0.18 | 84.2 | 13.7 | 0.018936 | 0 | 1 |  | 309.5277 | 305.7805 | -70.6748 | 8.0509 | -0.30147 |  | 143 | 116 | 86 | 61 | 29 | [7 empty] | 13.7 | 8 | 4.8 | 3 | 1.8 |  | 6.2277e-05 | 1.8358 |  | 77.1287 | 7.2063 | 0.21601 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZMW0.04107500/4
Horizontal Wall | Briza | BZMW.04109512/4 | 16.1 | 37.4 | 4pipe | 5.5 | 5395.7652 | 0.54 | 134.8 | 14.4 | 0.18406 | 0 | 1321.0453 | 1490.849 | 0.3 | 134.8 | 14.4 | 0.063343 | 0 | 1 |  | 1067.2269 | 80.7321 | -6.4343 | 0.96858 | 0 |  | 229 | 194 | 144 | 92 | 52 | [7 empty] | 14.4 | 8.4 | 5.7 | 3.4 | 2 |  | 8.9126e-05 | 1.8148 |  | 110.7169 | 21.4931 | -1.8007 | 0.13605 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZMW0.04109500/4
Horizontal Wall | Briza | BZMW.04112512/4 | 16.1 | 49.2 | 4pipe | 5.5 | 8566.9284 | 0.86 | 214.2 | 20.9 | 0.57827 | 0 | 2097.081 | 2366.6342 | 0.47 | 214.2 | 20.9 | 0.19319 | 0 | 1 |  | 1703.0145 | 114.9414 | -4.2359 | 1.0637 | 0 |  | 364 | 278 | 220 | 149 | 73 | [7 empty] | 20.9 | 12.6 | 7.4 | 4.1 | 2.3 |  | 0.00012049 | 1.8146 |  | 199.9546 | 22.2505 | -1.4664 | 0.17124 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZMW0.04112500/4
Horizontal Wall | Briza | BZMW.04114512/4 | 16.1 | 57.1 | 4pipe | 5.5 | 10683.2145 | 1.07 | 224.8 | 28.8 | 1.0007 | 0 | 2617.3158 | 2953.7385 | 0.59 | 224.8 | 28.8 | 0.33678 | 0 | 1 |  | 2025.6471 | 191.9198 | -10.1637 | 1.4268 | 0 |  | 382 | 289 | 227 | 158 | 89 | [7 empty] | 28.8 | 17 | 9 | 4.5 | 2.5 |  | 0.00012933 | 1.8293 |  | 228.6064 | 34.9076 | -2.3124 | 0.21152 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZMW0.04114500/4
Horizontal Wall | Briza | BZMW.05507512/4 | 21.7 | 29.5 | 4pipe | 5.5 | 2703.2655 | 0.27 | 100.6 | 10.3 | 0.077501 | 0 | 1168.3015 | 1318.4719 | 0.26 | 100.6 | 10.3 | 0.072374 | 0 | 1 |  | 361.3523 | 203.1299 | -50.9019 | 6.2288 | -0.24292 |  | 171 | 137 | 107 | 67 | 27 | [7 empty] | 10.3 | 6.3 | 3.6 | 2.2 | 1.6 |  | 0.00013264 | 1.8137 |  | 122.855 | 4.1514 | 1.8516 | -0.10048 | 0 |  | 0.00013264 | 1.8137 |  | D04 | BZMW0.05507500/4
Horizontal Wall | Briza | BZMW.05509512/4 | 21.7 | 37.4 | 4pipe | 5.5 | 4447.1714 | 0.44 | 151.3 | 15.6 | 0.2452 | 0 | 1933.9592 | 2182.5451 | 0.44 | 151.3 | 15.6 | 0.2452 | 0 | 1 |  | 758.5353 | 185.1317 | -41.8866 | 5.1948 | -0.1803 |  | 257 | 228 | 168 | 123 | 72 | [7 empty] | 15.6 | 10 | 5.9 | 3.4 | 2.1 |  | 0.00016748 | 1.8208 |  | 192.2611 | 12.8595 | 1.9707 | -0.10565 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZMW0.05509500/4
Horizontal Wall | Briza | BZMW.05512512/4 | 21.7 | 49.2 | 4pipe | 5.5 | 7061.9522 | 0.71 | 226.6 | 22.3 | 0.79136 | 0 | 3084.3925 | 3480.8521 | 0.7 | 226.6 | 22.3 | 0.77128 | 0 | 1 |  | 1146.735 | 307.8019 | -62.1251 | 7.5452 | -0.26785 |  | 385 | 328 | 260 | 183 | 112 | [7 empty] | 22.3 | 12.8 | 7.5 | 4.2 | 2.3 |  | 0.00023644 | 1.8121 |  | 292.4954 | 23.2566 | 3.337 | -0.20123 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZMW0.05512500/4
Horizontal Wall | Briza | BZMW.05514512/4 | 21.7 | 57.1 | 4pipe | 5.5 | 8808.1546 | 0.88 | 271.9 | 27.3 | 1.3658 | 0 | 3847.5124 | 4342.0613 | 0.87 | 271.9 | 27.3 | 1.3378 | 0 | 1 |  | 1716.3175 | 140.5341 | -6.6532 | 1.1345 | 0 |  | 462 | 393 | 304 | 228 | 126 | [7 empty] | 27.3 | 16 | 9.1 | 5.2 | 2.7 |  | 0.0002717 | 1.8154 |  | 414.9879 | 9.2617 | 6.5041 | -0.33781 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZMW0.05514500/4
Build-In | Briza Build-In Ceiling | BZBC.03805212 | 15 | 20.5 | 2pipe | 4.7 | 4503.7031 | 0.45 | 138.3 | 13 | 0.10182 | 0 | 1103.8298 | 1245.7132 | 0.25 | 138.3 | 13 | 0.03461 | 0 | 1 |  | 789.8652 | 134.6998 | -18.8973 | 2.1586 | -0.056967 |  | 235 | 196 | 155 | 111 | 70 | [7 empty] | 13 | 7.2 | 4.3 | 2.6 | 1.6 |  | 6.2277e-05 | 1.8358 |  | 84.4853 | 14.0455 | 0.10374 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZBC0.03805200
Build-In | Briza Build-In Ceiling | BZBC.03807212 | 15 | 28.3 | 2pipe | 4.7 | 7410.0948 | 0.74 | 223.7 | 18 | 0.32606 | 0 | 1817.4506 | 2051.0608 | 0.41 | 223.7 | 18 | 0.11166 | 0 | 1 |  | -15.1006 | 1373.1451 | -348.7213 | 38.1433 | -1.3967 |  | 380 | 315 | 245 | 189 | 119 | [7 empty] | 18 | 11.5 | 7.2 | 4.3 | 2.5 |  | 8.9126e-05 | 1.8148 |  | 169.3557 | 12.3037 | 0.9505 | 0 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZBC0.03807200
Build-In | Briza Build-In Ceiling | BZBC.03810212 | 15 | 40.2 | 2pipe | 4.7 | 11771.5028 | 1.18 | 289.6 | 24 | 1.0266 | 0 | 2882.6218 | 3253.1463 | 0.65 | 289.6 | 24 | 0.34794 | 0 | 1 |  | 12.5597 | 2180.469 | -556.9382 | 61.9307 | -2.3255 |  | 492 | 419 | 328 | 243 | 160 | [7 empty] | 24 | 14 | 8 | 4.8 | 2.6 |  | 0.00012049 | 1.8146 |  | 302.4141 | 7.0181 | 2.4192 | 0 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZBC0.03810200
Build-In | Briza Build-In Ceiling | BZBC.03812212 | 15 | 48 | 2pipe | 4.7 | 14675.5134 | 1.47 | 329.6 | 28.8 | 1.789 | 0 | 3581.2354 | 4041.5578 | 0.81 | 329.6 | 28.8 | 0.60134 | 0 | 1 |  | -11.0815 | 2760.9404 | -704.3095 | 78.375 | -2.956 |  | 560 | 512 | 410 | 295 | 190 | [7 empty] | 28.8 | 18.5 | 10.3 | 5.5 | 2.8 |  | 0.00012933 | 1.8293 |  | 482.8074 | -83.4063 | 21.0423 | -0.98953 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZBC0.03812200
Build-In | Briza Build-In Ceiling | BZBC.05205212 | 20.5 | 20.5 | 2pipe | 4.7 | 6664.4938 | 0.67 | 147.1 | 16.8 | 0.4029 | 0 | 1636.6191 | 1846.9858 | 0.37 | 147.1 | 16.8 | 0.13724 | 0 | 1 |  | 1799.5703 | -394.9724 | 154.9581 | -17.6097 | 0.6981 |  | 250 | 212 | 169 | 130 | 89 | [7 empty] | 16.8 | 9.6 | 5.5 | 3.2 | 2 |  | 0.00013264 | 1.8137 |  | 141.6189 | 31.0068 | -6.1453 | 1.0826 | -0.057083 |  | 0.00013264 | 1.8137 |  | D04 | BZBC0.05205200
Build-In | Briza Build-In Ceiling | BZBC.05207212 | 20.5 | 28.3 | 2pipe | 4.7 | 11035.5317 | 1.1 | 214.8 | 15.6 | 1.3005 | 0 | 2707.1872 | 3055.1618 | 0.61 | 214.8 | 15.6 | 0.44448 | 0 | 1 |  | 2449.9381 | -187.6716 | 122.058 | -13.2632 | 0.49831 |  | 365 | 320 | 262 | 193 | 127 | [7 empty] | 15.6 | 9.6 | 5.7 | 3.6 | 2.2 |  | 0.00016748 | 1.8208 |  | 278.2573 | 15.0039 | 3.0462 | -0.1558 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZBC0.05207200
Build-In | Briza Build-In Ceiling | BZBC.05210212 | 20.5 | 40.2 | 2pipe | 4.7 | 17592.2955 | 1.76 | 301.9 | 28.8 | 4.1001 | 0 | 4316.1515 | 4870.9381 | 0.97 | 301.9 | 28.8 | 1.3929 | 0 | 1 |  | 3667.2959 | -107.3225 | 136.6447 | -14.0765 | 0.49899 |  | 513 | 437 | 353 | 259 | 168 | [7 empty] | 28.8 | 18 | 10 | 5.4 | 2.8 |  | 0.00023644 | 1.8121 |  | 468.3656 | 4.1134 | 8.7424 | -0.46362 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZBC0.05210200
Build-In | Briza Build-In Ceiling | BZBC.05212212 | 20.5 | 48 | 2pipe | 4.7 | 21964.9158 | 2.19 | 343.1 | 28.8 | 7.149 | 0 | 5390.7668 | 6083.6815 | 1.22 | 343.1 | 28.8 | 2.4716 | 0 | 1 |  | 3546.9027 | 534.8842 | 10.7812 | -1.0194 | 0 |  | 583 | 500 | 396 | 297 | 200 | [7 empty] | 28.8 | 18 | 10 | 5.5 | 2.8 |  | 0.0002717 | 1.8154 |  | 613.1688 | -38.7073 | 28.3618 | -3.058 | 0.11449 |  | 0.0002717 | 1.8154 |  | D04 | BZBC0.05212200
Build-In | Briza Build-In Ceiling | BZBC.03805212/4 | 15 | 20.5 | 4pipe | 4.7 | 3602.0888 | 0.36 | 92.4 | 13.7 | 0.067598 | 0 | 881.3901 | 994.6816 | 0.2 | 92.4 | 13.7 | 0.022977 | 0 | 1 |  | 672.4156 | 69.7126 | -4.1131 | 0.51024 | 0 |  | 157 | 128 | 95 | 67 | 32 | [7 empty] | 13.7 | 8 | 4.8 | 3 | 1.8 |  | 6.2277e-05 | 1.8358 |  | 82.549 | 8.2878 | 0.22467 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZBC0.03805200/4
Build-In | Briza Build-In Ceiling | BZBC.03807212/4 | 15 | 28.3 | 4pipe | 4.7 | 5928.3973 | 0.59 | 148.3 | 14.4 | 0.21615 | 0 | 1453.3046 | 1640.1084 | 0.33 | 148.3 | 14.4 | 0.075304 | 0 | 1 |  | 1150.1568 | 117.5197 | -13.4762 | 1.4391 | 0 |  | 252 | 213 | 158 | 101 | 57 | [7 empty] | 14.4 | 8.4 | 5.7 | 3.4 | 2 |  | 8.9126e-05 | 1.8148 |  | 135.9908 | 15.3815 | -0.70553 | 0.090562 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZBC0.03807200/4
Build-In | Briza Build-In Ceiling | BZBC.03810212/4 | 15 | 40.2 | 4pipe | 4.7 | 9416.7753 | 0.94 | 235.4 | 20.9 | 0.67955 | 0 | 2305.8912 | 2602.2843 | 0.52 | 235.4 | 20.9 | 0.23209 | 0 | 1 |  | 1773.7133 | 185.7991 | -14.0646 | 1.6137 | 0 |  | 400 | 305 | 242 | 164 | 80 | [7 empty] | 20.9 | 12.6 | 7.4 | 4.1 | 2.3 |  | 0.00012049 | 1.8146 |  | 237.2471 | 17.1052 | -0.67547 | 0.15082 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZBC0.03810200/4
Build-In | Briza Build-In Ceiling | BZBC.03812212/4 | 15 | 48 | 4pipe | 4.7 | 11742.3518 | 1.17 | 247.2 | 28.8 | 1.1783 | 0 | 2869.9948 | 3238.8962 | 0.65 | 247.2 | 28.8 | 0.40206 | 0 | 1 |  | 2163.6048 | 249.058 | -17.7467 | 1.9075 | 0 |  | 420 | 318 | 249 | 174 | 98 | [7 empty] | 28.8 | 17 | 9 | 4.5 | 2.5 |  | 0.00012933 | 1.8293 |  | 283.0273 | 25.7017 | -1.042 | 0.17598 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZBC0.03812200/4
Build-In | Briza Build-In Ceiling | BZBC.05205212/4 | 20.5 | 20.5 | 4pipe | 4.7 | 2838.5164 | 0.28 | 110.7 | 10.3 | 0.082786 | 0 | 1227.9753 | 1385.816 | 0.28 | 110.7 | 10.3 | 0.082786 | 0 | 1 |  | 560.4282 | 40.9653 | -1.1471 | 0.30181 | 0 |  | 188 | 151 | 118 | 74 | 30 | [7 empty] | 10.3 | 6.3 | 3.6 | 2.2 | 1.6 |  | 0.00013264 | 1.8137 |  | 155.2937 | -22.9231 | 10.6485 | -1.1964 | 0.046731 |  | 0.00013264 | 1.8137 |  | D04 | BZBC0.05205200/4
Build-In | Briza Build-In Ceiling | BZBC.05207212/4 | 20.5 | 28.3 | 4pipe | 4.7 | 4667.7583 | 0.47 | 166 | 15.6 | 0.27649 | 0 | 2031.1724 | 2292.2539 | 0.46 | 166 | 15.6 | 0.26587 | 0 | 1 |  | 781.2038 | 203.9442 | -44.72 | 5.311 | -0.17567 |  | 282 | 251 | 185 | 135 | 79 | [7 empty] | 15.6 | 10 | 5.9 | 3.4 | 2.1 |  | 0.00016748 | 1.8208 |  | 197.7718 | 13.52 | 2.3588 | -0.13585 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZBC0.05207200/4
Build-In | Briza Build-In Ceiling | BZBC.05210212/4 | 20.5 | 40.2 | 4pipe | 4.7 | 7416.0921 | 0.74 | 249 | 22.3 | 0.85299 | 0 | 3238.9856 | 3655.3161 | 0.73 | 249 | 22.3 | 0.83221 | 0 | 1 |  | 1354.4189 | 174.2619 | -16.2569 | 1.552 | 0 |  | 423 | 360 | 286 | 201 | 123 | [7 empty] | 22.3 | 12.8 | 7.5 | 4.2 | 2.3 |  | 0.00023644 | 1.8121 |  | 381.7681 | -28.2505 | 17.4959 | -1.8214 | 0.066302 |  | 0.00023644 | 1.8121 |  | D04 | BZBC0.05210200/4
Build-In | Briza Build-In Ceiling | BZBC.05212212/4 | 20.5 | 48 | 4pipe | 4.7 | 9245.1751 | 0.92 | 299 | 27.3 | 1.4806 | 0 | 4041.493 | 4560.9757 | 0.91 | 299 | 27.3 | 1.4516 | 0 | 1 |  | 1396.9657 | 411.5965 | -68.3031 | 7.3274 | -0.2241 |  | 508 | 432 | 334 | 251 | 139 | [7 empty] | 27.3 | 16 | 9.1 | 5.2 | 2.7 |  | 0.0002717 | 1.8154 |  | 389.5552 | 30.9896 | 3.8853 | -0.22642 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZBC0.05212200/4
Build-In | Briza Build-In Wall | BZBW.03805212 | 15 | 20.5 | 2pipe | 4.7 | 4503.7031 | 0.45 | 138.3 | 13 | 0.10182 | 0 | 1103.8298 | 1245.7132 | 0.25 | 138.3 | 13 | 0.03461 | 0 | 1 |  | 789.8652 | 134.6998 | -18.8973 | 2.1586 | -0.056967 |  | 235 | 196 | 155 | 111 | 70 | [7 empty] | 13 | 7.2 | 4.3 | 2.6 | 1.6 |  | 6.2277e-05 | 1.8358 |  | 84.4853 | 14.0455 | 0.10374 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZBW0.03805200
Build-In | Briza Build-In Wall | BZBW.03807212 | 15 | 28.3 | 2pipe | 4.7 | 7410.0948 | 0.74 | 223.7 | 18 | 0.32606 | 0 | 1817.4506 | 2051.0608 | 0.41 | 223.7 | 18 | 0.11166 | 0 | 1 |  | -15.1006 | 1373.1451 | -348.7213 | 38.1433 | -1.3967 |  | 380 | 315 | 245 | 189 | 119 | [7 empty] | 18 | 11.5 | 7.2 | 4.3 | 2.5 |  | 8.9126e-05 | 1.8148 |  | 169.3557 | 12.3037 | 0.9505 | 0 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZBW0.03807200
Build-In | Briza Build-In Wall | BZBW.03810212 | 15 | 40.2 | 2pipe | 4.7 | 11771.5028 | 1.18 | 289.6 | 24 | 1.0266 | 0 | 2882.6218 | 3253.1463 | 0.65 | 289.6 | 24 | 0.34794 | 0 | 1 |  | 12.5597 | 2180.469 | -556.9382 | 61.9307 | -2.3255 |  | 492 | 419 | 328 | 243 | 160 | [7 empty] | 24 | 14 | 8 | 4.8 | 2.6 |  | 0.00012049 | 1.8146 |  | 302.4141 | 7.0181 | 2.4192 | 0 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZBW0.03810200
Build-In | Briza Build-In Wall | BZBW.03812212 | 15 | 48 | 2pipe | 4.7 | 14675.5134 | 1.47 | 329.6 | 28.8 | 1.789 | 0 | 3581.2354 | 4041.5578 | 0.81 | 329.6 | 28.8 | 0.60134 | 0 | 1 |  | -11.0815 | 2760.9404 | -704.3095 | 78.375 | -2.956 |  | 560 | 512 | 410 | 295 | 190 | [7 empty] | 28.8 | 18.5 | 10.3 | 5.5 | 2.8 |  | 0.00012933 | 1.8293 |  | 482.8074 | -83.4063 | 21.0423 | -0.98953 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZBW0.03812200
Build-In | Briza Build-In Wall | BZBW.05205212 | 20.5 | 20.5 | 2pipe | 4.7 | 6664.4938 | 0.67 | 147.1 | 16.8 | 0.4029 | 0 | 1636.6191 | 1846.9858 | 0.37 | 147.1 | 16.8 | 0.13724 | 0 | 1 |  | 1799.5703 | -394.9724 | 154.9581 | -17.6097 | 0.6981 |  | 250 | 212 | 169 | 130 | 89 | [7 empty] | 16.8 | 9.6 | 5.5 | 3.2 | 2 |  | 0.00013264 | 1.8137 |  | 141.6189 | 31.0068 | -6.1453 | 1.0826 | -0.057083 |  | 0.00013264 | 1.8137 |  | D04 | BZBW0.05205200
Build-In | Briza Build-In Wall | BZBW.05207212 | 20.5 | 28.3 | 2pipe | 4.7 | 11035.5317 | 1.1 | 214.8 | 15.6 | 1.3005 | 0 | 2707.1872 | 3055.1618 | 0.61 | 214.8 | 15.6 | 0.44448 | 0 | 1 |  | 2449.9381 | -187.6716 | 122.058 | -13.2632 | 0.49831 |  | 365 | 320 | 262 | 193 | 127 | [7 empty] | 15.6 | 9.6 | 5.7 | 3.6 | 2.2 |  | 0.00016748 | 1.8208 |  | 278.2573 | 15.0039 | 3.0462 | -0.1558 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZBW0.05207200
Build-In | Briza Build-In Wall | BZBW.05210212 | 20.5 | 40.2 | 2pipe | 4.7 | 17592.2955 | 1.76 | 301.9 | 28.8 | 4.1001 | 0 | 4316.1515 | 4870.9381 | 0.97 | 301.9 | 28.8 | 1.3929 | 0 | 1 |  | 3667.2959 | -107.3225 | 136.6447 | -14.0765 | 0.49899 |  | 513 | 437 | 353 | 259 | 168 | [7 empty] | 28.8 | 18 | 10 | 5.4 | 2.8 |  | 0.00023644 | 1.8121 |  | 468.3656 | 4.1134 | 8.7424 | -0.46362 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZBW0.05210200
Build-In | Briza Build-In Wall | BZBW.05212212 | 20.5 | 48 | 2pipe | 4.7 | 21964.9158 | 2.19 | 343.1 | 28.8 | 7.149 | 0 | 5390.7668 | 6083.6815 | 1.22 | 343.1 | 28.8 | 2.4716 | 0 | 1 |  | 3546.9027 | 534.8842 | 10.7812 | -1.0194 | 0 |  | 583 | 500 | 396 | 297 | 200 | [7 empty] | 28.8 | 18 | 10 | 5.5 | 2.8 |  | 0.0002717 | 1.8154 |  | 613.1688 | -38.7073 | 28.3618 | -3.058 | 0.11449 |  | 0.0002717 | 1.8154 |  | D04 | BZBW0.05212200
Build-In | Briza Build-In Wall | BZBW.03805212/4 | 15 | 20.5 | 4pipe | 4.7 | 3602.0888 | 0.36 | 92.4 | 13.7 | 0.067598 | 0 | 881.3901 | 994.6816 | 0.2 | 92.4 | 13.7 | 0.022977 | 0 | 1 |  | 672.4156 | 69.7126 | -4.1131 | 0.51024 | 0 |  | 157 | 128 | 95 | 67 | 32 | [7 empty] | 13.7 | 8 | 4.8 | 3 | 1.8 |  | 6.2277e-05 | 1.8358 |  | 82.549 | 8.2878 | 0.22467 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZBW0.03805200/4
Build-In | Briza Build-In Wall | BZBW.03807212/4 | 15 | 28.3 | 4pipe | 4.7 | 5928.3973 | 0.59 | 148.3 | 14.4 | 0.21615 | 0 | 1453.3046 | 1640.1084 | 0.33 | 148.3 | 14.4 | 0.075304 | 0 | 1 |  | 1150.1568 | 117.5197 | -13.4762 | 1.4391 | 0 |  | 252 | 213 | 158 | 101 | 57 | [7 empty] | 14.4 | 8.4 | 5.7 | 3.4 | 2 |  | 8.9126e-05 | 1.8148 |  | 135.9908 | 15.3815 | -0.70553 | 0.090562 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZBW0.03807200/4
Build-In | Briza Build-In Wall | BZBW.03810212/4 | 15 | 40.2 | 4pipe | 4.7 | 9416.7753 | 0.94 | 235.4 | 20.9 | 0.67955 | 0 | 2305.8912 | 2602.2843 | 0.52 | 235.4 | 20.9 | 0.23209 | 0 | 1 |  | 1773.7133 | 185.7991 | -14.0646 | 1.6137 | 0 |  | 400 | 305 | 242 | 164 | 80 | [7 empty] | 20.9 | 12.6 | 7.4 | 4.1 | 2.3 |  | 0.00012049 | 1.8146 |  | 237.2471 | 17.1052 | -0.67547 | 0.15082 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZBW0.03810200/4
Build-In | Briza Build-In Wall | BZBW.03812212/4 | 15 | 48 | 4pipe | 4.7 | 11742.3518 | 1.17 | 247.2 | 28.8 | 1.1783 | 0 | 2869.9948 | 3238.8962 | 0.65 | 247.2 | 28.8 | 0.40206 | 0 | 1 |  | 2163.6048 | 249.058 | -17.7467 | 1.9075 | 0 |  | 420 | 318 | 249 | 174 | 98 | [7 empty] | 28.8 | 17 | 9 | 4.5 | 2.5 |  | 0.00012933 | 1.8293 |  | 283.0273 | 25.7017 | -1.042 | 0.17598 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZBW0.03812200/4
Build-In | Briza Build-In Wall | BZBW.05205212/4 | 20.5 | 20.5 | 4pipe | 4.7 | 2838.5164 | 0.28 | 110.7 | 10.3 | 0.082786 | 0 | 1227.9753 | 1385.816 | 0.28 | 110.7 | 10.3 | 0.082786 | 0 | 1 |  | 560.4282 | 40.9653 | -1.1471 | 0.30181 | 0 |  | 188 | 151 | 118 | 74 | 30 | [7 empty] | 10.3 | 6.3 | 3.6 | 2.2 | 1.6 |  | 0.00013264 | 1.8137 |  | 155.2937 | -22.9231 | 10.6485 | -1.1964 | 0.046731 |  | 0.00013264 | 1.8137 |  | D04 | BZBW0.05205200/4
Build-In | Briza Build-In Wall | BZBW.05207212/4 | 20.5 | 28.3 | 4pipe | 4.7 | 4667.7583 | 0.47 | 166 | 15.6 | 0.27649 | 0 | 2031.1724 | 2292.2539 | 0.46 | 166 | 15.6 | 0.26587 | 0 | 1 |  | 781.2038 | 203.9442 | -44.72 | 5.311 | -0.17567 |  | 282 | 251 | 185 | 135 | 79 | [7 empty] | 15.6 | 10 | 5.9 | 3.4 | 2.1 |  | 0.00016748 | 1.8208 |  | 197.7718 | 13.52 | 2.3588 | -0.13585 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZBW0.05207200/4
Build-In | Briza Build-In Wall | BZBW.05210212/4 | 20.5 | 40.2 | 4pipe | 4.7 | 7416.0921 | 0.74 | 249 | 22.3 | 0.85299 | 0 | 3238.9856 | 3655.3161 | 0.73 | 249 | 22.3 | 0.83221 | 0 | 1 |  | 1354.4189 | 174.2619 | -16.2569 | 1.552 | 0 |  | 423 | 360 | 286 | 201 | 123 | [7 empty] | 22.3 | 12.8 | 7.5 | 4.2 | 2.3 |  | 0.00023644 | 1.8121 |  | 381.7681 | -28.2505 | 17.4959 | -1.8214 | 0.066302 |  | 0.00023644 | 1.8121 |  | D04 | BZBW0.05210200/4
Build-In | Briza Build-In Wall | BZBW.05212212/4 | 20.5 | 48 | 4pipe | 4.7 | 9245.1751 | 0.92 | 299 | 27.3 | 1.4806 | 0 | 4041.493 | 4560.9757 | 0.91 | 299 | 27.3 | 1.4516 | 0 | 1 |  | 1396.9657 | 411.5965 | -68.3031 | 7.3274 | -0.2241 |  | 508 | 432 | 334 | 251 | 139 | [7 empty] | 27.3 | 16 | 9.1 | 5.2 | 2.7 |  | 0.0002717 | 1.8154 |  | 389.5552 | 30.9896 | 3.8853 | -0.22642 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZBW0.05212200/4
Ceiling | Briza Ceiling | BZMC.04107512 | 16.1 | 29.5 | 2pipe | 5.5 | 4094.7646 | 0.41 | 126 | 13 | 0.085827 | 0 | 1004.2217 | 1133.3016 | 0.23 | 126 | 13 | 0.029698 | 0 | 1 |  | 784.0931 | 57.9733 | 0.1949 | 0.21174 | 0.0074264 |  | 214 | 178 | 141 | 101 | 64 | [7 empty] | 13 | 7.2 | 4.3 | 2.6 | 1.6 |  | 6.2277e-05 | 1.8358 |  | 102.0759 | 4.9047 | 0.93056 | -0.0301 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZMC0.04107500
Ceiling | Briza Ceiling | BZMC.04109512 | 16.1 | 37.4 | 2pipe | 5.5 | 6743.7123 | 0.67 | 203.6 | 18 | 0.27226 | 0 | 1652.9378 | 1865.402 | 0.37 | 203.6 | 18 | 0.092681 | 0 | 1 |  | 237.1457 | 1211.6861 | -360.6249 | 44.4855 | -1.8028 |  | 346 | 287 | 223 | 172 | 108 | [7 empty] | 18 | 11.5 | 7.2 | 4.3 | 2.5 |  | 8.9126e-05 | 1.8148 |  | 173.5639 | 6.8789 | 0.95253 | 0.014766 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZMC0.04109500
Ceiling | Briza Ceiling | BZMC.04112512 | 16.1 | 49.2 | 2pipe | 5.5 | 10711.4204 | 1.07 | 263.7 | 24 | 0.85962 | 0 | 2620.9816 | 2957.8755 | 0.59 | 263.7 | 24 | 0.29187 | 0 | 1 |  | 2161.5461 | 142.0685 | -6.6767 | 1.4786 | -0.0026387 |  | 448 | 381 | 298 | 221 | 146 | [7 empty] | 24 | 14 | 8 | 4.8 | 2.6 |  | 0.00012049 | 1.8146 |  | 290.7155 | 9.4024 | 0.7828 | 0.095719 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZMC0.04112500
Ceiling | Briza Ceiling | BZMC.04114512 | 16.1 | 57.1 | 2pipe | 5.5 | 13353.2454 | 1.33 | 300.2 | 28.8 | 1.4897 | 0 | 3272.0821 | 3692.6668 | 0.74 | 300.2 | 28.8 | 0.5097 | 0 | 1 |  | 2614.5642 | 199.5924 | -6.7862 | 1.5119 | 0 |  | 510 | 466 | 373 | 268 | 173 | [7 empty] | 28.8 | 18.5 | 10.3 | 5.5 | 2.8 |  | 0.00012933 | 1.8293 |  | 379.7621 | 15.6645 | -0.25189 | 0.18632 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZMC0.04114500
Ceiling | Briza Ceiling | BZMC.05507512 | 21.7 | 29.5 | 2pipe | 5.5 | 6349.1031 | 0.63 | 134.2 | 16.8 | 0.36033 | 0 | 1558.3339 | 1758.638 | 0.35 | 134.2 | 16.8 | 0.12409 | 0 | 1 |  | 1095.2129 | 152.8798 | -0.35664 | 0 | 0 |  | 228 | 193 | 154 | 118 | 81 | [7 empty] | 16.8 | 9.6 | 5.5 | 3.2 | 2 |  | 0.00013264 | 1.8137 |  | 124.6876 | 22.688 | -0.072116 | -0.002007 | -0.0010144 |  | 0.00013264 | 1.8137 |  | D04 | BZMC0.05507500
Ceiling | Briza Ceiling | BZMC.05509512 | 21.7 | 37.4 | 2pipe | 5.5 | 10510.3157 | 1.05 | 195.4 | 15.6 | 1.1948 | 0 | 2580.9092 | 2912.6524 | 0.58 | 195.4 | 15.6 | 0.40549 | 0 | 1 |  | 1733.6903 | 251.4329 | 4.0609 | -0.36935 | 0 |  | 332 | 291 | 238 | 176 | 116 | [7 empty] | 15.6 | 9.6 | 5.7 | 3.6 | 2.2 |  | 0.00016748 | 1.8208 |  | 244.8221 | 20.927 | 2.4216 | -0.14606 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZMC0.05509500
Ceiling | Briza Ceiling | BZMC.05512512 | 21.7 | 49.2 | 2pipe | 5.5 | 16755.1906 | 1.67 | 274.9 | 28.8 | 3.7281 | 0 | 4113.8381 | 4642.6199 | 0.93 | 274.9 | 28.8 | 1.2906 | 0 | 1 |  | 2743.7411 | 390.8208 | 10.6017 | -0.88151 | 0 |  | 467 | 398 | 321 | 236 | 153 | [7 empty] | 28.8 | 18 | 10 | 5.4 | 2.8 |  | 0.00023644 | 1.8121 |  | 404.4386 | 26.677 | 4.6735 | -0.26157 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZMC0.05512500
Ceiling | Briza Ceiling | BZMC.05514512 | 21.7 | 57.1 | 2pipe | 5.5 | 20913.2128 | 2.09 | 312.5 | 28.8 | 6.5675 | 0 | 5138.0931 | 5798.5298 | 1.16 | 312.5 | 28.8 | 2.2553 | 0 | 1 |  | 3621.1756 | 398.101 | 26.2681 | -1.7033 | 0 |  | 531 | 455 | 360 | 270 | 182 | [7 empty] | 28.8 | 18 | 10 | 5.5 | 2.8 |  | 0.0002717 | 1.8154 |  | 500.4299 | 34.9711 | 5.5713 | -0.31193 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZMC0.05514500
Ceiling | Briza Ceiling | BZMC.04107512/4 | 16.1 | 29.5 | 4pipe | 5.5 | 3277.2674 | 0.33 | 84.2 | 13.7 | 0.057618 | 0 | 801.1687 | 904.1487 | 0.18 | 84.2 | 13.7 | 0.018936 | 0 | 1 |  | 309.5277 | 305.7805 | -70.6748 | 8.0509 | -0.30147 |  | 143 | 116 | 86 | 61 | 29 | [7 empty] | 13.7 | 8 | 4.8 | 3 | 1.8 |  | 6.2277e-05 | 1.8358 |  | 77.1287 | 7.2063 | 0.21601 | 0 | 0 |  | 6.2277e-05 | 1.8358 |  | D04 | BZMC0.04107500/4
Ceiling | Briza Ceiling | BZMC.04109512/4 | 16.1 | 37.4 | 4pipe | 5.5 | 5395.7652 | 0.54 | 134.8 | 14.4 | 0.18406 | 0 | 1321.0453 | 1490.849 | 0.3 | 134.8 | 14.4 | 0.063343 | 0 | 1 |  | 1067.2269 | 80.7321 | -6.4343 | 0.96858 | 0 |  | 229 | 194 | 144 | 92 | 52 | [7 empty] | 14.4 | 8.4 | 5.7 | 3.4 | 2 |  | 8.9126e-05 | 1.8148 |  | 110.7169 | 21.4931 | -1.8007 | 0.13605 | 0 |  | 8.9126e-05 | 1.8148 |  | D04 | BZMC0.04109500/4
Ceiling | Briza Ceiling | BZMC.04112512/4 | 16.1 | 49.2 | 4pipe | 5.5 | 8566.9284 | 0.86 | 214.2 | 20.9 | 0.57827 | 0 | 2097.081 | 2366.6342 | 0.47 | 214.2 | 20.9 | 0.19319 | 0 | 1 |  | 1703.0145 | 114.9414 | -4.2359 | 1.0637 | 0 |  | 364 | 278 | 220 | 149 | 73 | [7 empty] | 20.9 | 12.6 | 7.4 | 4.1 | 2.3 |  | 0.00012049 | 1.8146 |  | 199.9546 | 22.2505 | -1.4664 | 0.17124 | 0 |  | 0.00012049 | 1.8146 |  | D04 | BZMC0.04112500/4
Ceiling | Briza Ceiling | BZMC.04114512/4 | 16.1 | 57.1 | 4pipe | 5.5 | 10683.2145 | 1.07 | 224.8 | 28.8 | 1.0007 | 0 | 2617.3158 | 2953.7385 | 0.59 | 224.8 | 28.8 | 0.33678 | 0 | 1 |  | 2025.6471 | 191.9198 | -10.1637 | 1.4268 | 0 |  | 382 | 289 | 227 | 158 | 89 | [7 empty] | 28.8 | 17 | 9 | 4.5 | 2.5 |  | 0.00012933 | 1.8293 |  | 228.6064 | 34.9076 | -2.3124 | 0.21152 | 0 |  | 0.00012933 | 1.8293 |  | D04 | BZMC0.04114500/4
Ceiling | Briza Ceiling | BZMC.05507512/4 | 21.7 | 29.5 | 4pipe | 5.5 | 2703.2655 | 0.27 | 100.6 | 10.3 | 0.077501 | 0 | 1168.3015 | 1318.4719 | 0.26 | 100.6 | 10.3 | 0.072374 | 0 | 1 |  | 361.3523 | 203.1299 | -50.9019 | 6.2288 | -0.24292 |  | 171 | 137 | 107 | 67 | 27 | [7 empty] | 10.3 | 6.3 | 3.6 | 2.2 | 1.6 |  | 0.00013264 | 1.8137 |  | 122.855 | 4.1514 | 1.8516 | -0.10048 | 0 |  | 0.00013264 | 1.8137 |  | D04 | BZMC0.05507500/4
Ceiling | Briza Ceiling | BZMC.05509512/4 | 21.7 | 37.4 | 4pipe | 5.5 | 4447.1714 | 0.44 | 151.3 | 15.6 | 0.2452 | 0 | 1933.9592 | 2182.5451 | 0.44 | 151.3 | 15.6 | 0.2452 | 0 | 1 |  | 758.5353 | 185.1317 | -41.8866 | 5.1948 | -0.1803 |  | 257 | 228 | 168 | 123 | 72 | [7 empty] | 15.6 | 10 | 5.9 | 3.4 | 2.1 |  | 0.00016748 | 1.8208 |  | 192.2611 | 12.8595 | 1.9707 | -0.10565 | 0 |  | 0.00016748 | 1.8208 |  | D04 | BZMC0.05509500/4
Ceiling | Briza Ceiling | BZMC.05512512/4 | 21.7 | 49.2 | 4pipe | 5.5 | 7061.9522 | 0.71 | 226.6 | 22.3 | 0.79136 | 0 | 3084.3925 | 3480.8521 | 0.7 | 226.6 | 22.3 | 0.77128 | 0 | 1 |  | 1146.735 | 307.8019 | -62.1251 | 7.5452 | -0.26785 |  | 385 | 328 | 260 | 183 | 112 | [7 empty] | 22.3 | 12.8 | 7.5 | 4.2 | 2.3 |  | 0.00023644 | 1.8121 |  | 292.4954 | 23.2566 | 3.337 | -0.20123 | 0 |  | 0.00023644 | 1.8121 |  | D04 | BZMC0.05512500/4
Ceiling | Briza Ceiling | BZMC.05514512/4 | 21.7 | 57.1 | 4pipe | 5.5 | 8808.1546 | 0.88 | 271.9 | 27.3 | 1.3658 | 0 | 3847.5124 | 4342.0613 | 0.87 | 271.9 | 27.3 | 1.3378 | 0 | 1 |  | 1716.3175 | 140.5341 | -6.6532 | 1.1345 | 0 |  | 462 | 393 | 304 | 228 | 126 | [7 empty] | 27.3 | 16 | 9.1 | 5.2 | 2.7 |  | 0.0002717 | 1.8154 |  | 414.9879 | 9.2617 | 6.5041 | -0.33781 | 0 |  | 0.0002717 | 1.8154 |  | D04 | BZMC0.05514500/4

## Clima Canal
Selection Model 2022-10 | [51 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF |  |  |  | Entering T | 45 | EWT ºF |  |  |  |  | 7.2222 | [31 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF |  |  |  | Return T | 55 | LWT ºF |  |  |  |  | 12.7778 |  |  | p_atm |  | h(mm) | 0 | [25 empty] | retour | 18 | ºC | A = | 0.88329
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF |  |  |  | Air T | 75 | AT ºF |  |  |  |  | 23.8889 |  |  | 101325 |  | cf_h | 1 | [25 empty] | ruimte | 27 | ºC | Td = | 12.8127
[7 empty] | Mean T | 130 | ºF |  |  |  | Mean T | 50 | ºF |  |  |  |  | -13.7017 | -9.9666 | [31 empty] | -10
[13 empty] | Rel Humid | 50%
[7 empty] | Fanspeed | 100% |  |  |  |  | Fanspeed | 100% |  |  |  |  | *Sound pressure with an assumed room damping of 8dB(A) | [33 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º | [5 empty] | 45/55/75º (50% RH) | [6 empty] | N-Waarde | [5 empty] | 75/65/20ºC | [5 empty] | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pressure Drop |  |  | 16/18/27ºC | [5 empty] | Pressure Drop
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | Sensible Cooling in BTU/h | Total Cooling in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | a | b | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | a | b | Kolom | SalesGroup | JagaSourceCode Stnd
Build-In Floor | Clima Canal 08 | CLCM.00807218/BNA | 3.34 | 28.3 | 2pipe | 7.1 | 2637 | 0.26 | 46.5 | 3 | 0.14568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 1075 | 891 | 699 | 496 | 276 |  | 79 | 68 | 52 | 37 | 24 | [7 empty] | 3 | 2.1 | 1.3 | 0.8 | 0.5 |  | 0.0002565 | 1.8235 |  | 185 | 144 | 104 | 66 | 30 |  |  |  |  | A12 | CLCM0.00807218/BNA
Build-In Floor | Clima Canal 08 | CLCM.00810818/BNA | 3.34 | 42.5 | 2pipe | 7.1 | 5431 | 0.54 | 94.2 | 7.1 | 0.86576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 2214 | 1834 | 1438 | 1021 | 569 |  | 160 | 125 | 98 | 75 | 42 | [7 empty] | 7.1 | 4.6 | 2.7 | 1.3 | 0.6 |  | 0.00040202 | 1.8235 |  | 381 | 296 | 214 | 135 | 62 |  |  |  |  | A12 | CLCM0.00810818/BNA
Build-In Floor | Clima Canal 08 | CLCM.00814418/BNA | 3.34 | 56.7 | 2pipe | 7.1 | 8534 | 0.85 | 140.7 | 10.1 | 2.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 3479 | 2881 | 2260 | 1605 | 894 |  | 239 | 193 | 150 | 112 | 66 | [7 empty] | 10.1 | 6.6 | 4 | 2.1 | 1.1 |  | 0.00056055 | 1.8235 |  | 598 | 465 | 336 | 212 | 97 |  |  |  |  | A12 | CLCM0.00814418/BNA
Build-In Floor | Clima Canal 08 | CLCM.00818018/BNA | 3.34 | 70.9 | 2pipe | 7.1 | 11637 | 1.16 | 188.3 | 14.1 | 6.4246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 4744 | 3929 | 3082 | 2188 | 1219 |  | 320 | 250 | 196 | 150 | 84 | [7 empty] | 14.1 | 9.1 | 5.4 | 2.5 | 1.2 |  | 0.0007399 | 1.8235 |  | 816 | 634 | 458 | 290 | 132 |  |  |  |  | A12 | CLCM0.00818018/BNA
Build-In Floor | Clima Canal 10 | CLCM.01007218/BNA | 3.9 | 28.3 | 2pipe | 7.1 | 2637 | 0.26 | 46.5 | 3 | 0.14568 | 0 | 843 | 951.357 | 0.19 | 46.5 | 3 | 0.082227 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 1075 | 891 | 699 | 496 | 276 |  | 79 | 68 | 52 | 37 | 24 | [7 empty] | 3 | 2.1 | 1.3 | 0.8 | 0.5 |  | 0.0002565 | 1.8235 |  | 185 | 144 | 104 | 66 | 30 |  |  |  |  | A12 | CLCM0.01007218/BNA
Build-In Floor | Clima Canal 10 | CLCM.01010818/BNA | 3.9 | 42.5 | 2pipe | 7.1 | 5431 | 0.54 | 94.2 | 7.1 | 0.86576 | 0 | 1737 | 1960.2693 | 0.39 | 94.2 | 7.1 | 0.47828 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 2214 | 1834 | 1438 | 1021 | 569 |  | 160 | 125 | 98 | 75 | 42 | [7 empty] | 7.1 | 4.6 | 2.7 | 1.3 | 0.6 |  | 0.00040202 | 1.8235 |  | 381 | 296 | 214 | 135 | 62 |  |  |  |  | A12 | CLCM0.01010818/BNA
Build-In Floor | Clima Canal 10 | CLCM.01014418/BNA | 3.9 | 56.7 | 2pipe | 7.1 | 8534 | 0.85 | 140.7 | 10.1 | 2.7608 | 0 | 2726 | 3076.3927 | 0.62 | 140.7 | 10.1 | 1.553 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 3479 | 2881 | 2260 | 1605 | 894 |  | 239 | 193 | 150 | 112 | 66 | [7 empty] | 10.1 | 6.6 | 4 | 2.1 | 1.1 |  | 0.00056055 | 1.8235 |  | 598 | 465 | 336 | 212 | 97 |  |  |  |  | A12 | CLCM0.01014418/BNA
Build-In Floor | Clima Canal 10 | CLCM.01018018/BNA | 3.9 | 70.9 | 2pipe | 7.1 | 11637 | 1.16 | 188.3 | 14.1 | 6.4246 | 0 | 3720 | 4198.1588 | 0.84 | 188.3 | 14.1 | 3.5664 | 0 | 0.91 | 0.87 | 0.79 | 0.68 | 0.6 |  | 4744 | 3929 | 3082 | 2188 | 1219 |  | 320 | 250 | 196 | 150 | 84 | [7 empty] | 14.1 | 9.1 | 5.4 | 2.5 | 1.2 |  | 0.0007399 | 1.8235 |  | 816 | 634 | 458 | 290 | 132 |  |  |  |  | A12 | CLCM0.01018018/BNA
Build-In Floor | Clima Canal H13 | CCLF.01307032/BNA | 5.1 | 27.6 | 2pipe | 12.6 | 3904 | 0.39 | 80.6 | 8.8 | 0.037155 | 0 | 1184 | 1336.1882 | 0.27 | 80.6 | 8.8 | 0.018331 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 1591.6107 | 1331.1833 | 1031.2359 | 691.7684 | 312.7809 |  | 137 | 117 | 85 | 44 | 35 | [7 empty] | 8.8 | 5.9 | 3.2 | 1.632 | 0.984 |  | 2.0145e-05 | 1.9213 |  | 271.4437 | 224.2801 | 174.5361 | 122.2115 | 67.3064 |  | 2.0145e-05 | 1.9213 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01310032/BNA | 5.1 | 39.4 | 2pipe | 12.6 | 7400 | 0.74 | 118.9 | 10.3 | 0.15859 | 0 | 2244 | 2532.4378 | 0.51 | 118.9 | 10.3 | 0.078467 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 3016.9338 | 2523.2878 | 1954.7307 | 1311.2625 | 592.8831 |  | 202 | 168 | 133 | 85 | 44 | [7 empty] | 10.3 | 6.4 | 3.2 | 1.8 | 1.008 |  | 2.944e-05 | 1.8903 |  | 514.5276 | 425.128 | 330.837 | 231.6546 | 127.5807 |  | 2.944e-05 | 1.8903 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01312032/BNA | 5.1 | 47.2 | 2pipe | 12.6 | 9731 | 0.97 | 160.7 | 10.6 | 0.29824 | 0 | 2951 | 3330.3136 | 0.67 | 160.7 | 10.6 | 0.14903 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 3967.1491 | 3318.0242 | 2570.394 | 1724.2586 | 779.618 |  | 273 | 235 | 174 | 114 | 49 | [7 empty] | 10.6 | 7.2 | 4.2 | 2.4 | 1.4 |  | 3.6052e-05 | 1.875 |  | 676.5835 | 559.0266 | 435.0377 | 304.6167 | 167.7636 |  | 3.6052e-05 | 1.875 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01314032/BNA | 5.1 | 55.1 | 2pipe | 12.6 | 12062 | 1.21 | 199.5 | 19.1 | 0.50142 | 0 | 3658 | 4128.1895 | 0.83 | 199.5 | 19.1 | 0.24853 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 4917.3645 | 4112.7605 | 3186.0572 | 2137.2546 | 966.3528 |  | 339 | 285 | 218 | 129 | 79 | [7 empty] | 19.1 | 12.3 | 6.4 | 3.432 | 1.992 |  | 4.3073e-05 | 1.862 |  | 838.6394 | 692.9252 | 539.2383 | 377.5788 | 207.9466 |  | 4.3073e-05 | 1.862 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01317032/BNA | 5.1 | 66.9 | 2pipe | 12.6 | 15558 | 1.56 | 241.3 | 19.4 | 0.92129 | 0 | 4718 | 5324.4391 | 1.06 | 241.3 | 19.4 | 0.45134 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 6342.6875 | 5304.865 | 4109.552 | 2756.7487 | 1246.4551 |  | 410 | 352 | 259 | 158 | 84 | [7 empty] | 19.4 | 13.1 | 7.4 | 4.032 | 2.384 |  | 5.3974e-05 | 1.8466 |  | 1081.7233 | 893.7731 | 695.5393 | 487.0219 | 268.2209 |  | 5.3974e-05 | 1.8466 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01320032/BNA | 5.1 | 78.7 | 2pipe | 12.6 | 19055 | 1.91 | 279.6 | 20.9 | 1.5039 | 0 | 5778 | 6520.6887 | 1.3 | 279.6 | 20.9 | 0.74233 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 7768.0106 | 6496.9694 | 5033.0469 | 3376.2428 | 1526.5574 |  | 475 | 403 | 307 | 199 | 93 | [7 empty] | 20.9 | 13.6 | 7.4 | 4.2 | 2.408 |  | 6.5019e-05 | 1.8351 |  | 1324.8072 | 1094.621 | 851.8402 | 596.465 | 328.4953 |  | 6.5019e-05 | 1.8351 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01323032/BNA | 5.1 | 90.6 | 2pipe | 12.6 | 22551 | 2.26 | 321.4 | 21.2 | 2.2698 | 0 | 6838 | 7716.9382 | 1.54 | 321.4 | 21.2 | 1.1269 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 9193.3336 | 7689.0739 | 5956.5417 | 3995.7369 | 1806.6596 |  | 546 | 470 | 348 | 228 | 98 | [7 empty] | 21.2 | 14.4 | 8.4 | 4.8 | 2.8 |  | 7.6584e-05 | 1.8254 |  | 1567.8911 | 1295.4689 | 1008.1412 | 705.9081 | 388.7696 |  | 7.6584e-05 | 1.8254 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01328032/BNA | 5.1 | 110.2 | 2pipe | 12.6 | 28378 | 2.84 | 402 | 30 | 3.9944 | 0 | 8605 | 9711.0637 | 1.94 | 402 | 30 | 2.0024 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 11568.872 | 9675.9147 | 7495.6998 | 5028.2271 | 2273.4967 |  | 683 | 587 | 433 | 272 | 133 | [7 empty] | 30 | 20.3 | 11.6 | 6.432 | 3.784 |  | 9.6911e-05 | 1.8119 |  | 1973.031 | 1630.2154 | 1268.6428 | 888.3133 | 489.2269 |  | 9.6911e-05 | 1.8119 |  | D15
Build-In Floor | Clima Canal H13 | CCLF.01330032/BNA | 5.1 | 118.1 | 2pipe | 12.6 | 30709 | 3.07 | 440.3 | 38.8 | 4.7484 | 0 | 9312 | 10508.9396 | 2.1 | 440.3 | 38.8 | 2.3877 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 12519.2 | 10470.7 | 8111.3 | 5441.28 | 2460.22 |  | 748 | 638 | 481 | 313 | 142 | [7 empty] | 38.8 | 26.2 | 14.8 | 8 | 4.8 |  | 0.00010104 | 1.8104 |  | 2135.09 | 1764.11 | 1372.83 | 961.27 | 529.396 |  | 0.00010104 | 1.8104 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01307032/BNA | 5.1 | 27.6 | 4pipe | 12.6 | 2582 | 0.26 | 80.6 | 8.8 | 0.024516 | 0 | 1166 | 1315.8745 | 0.26 | 80.6 | 8.8 | 0.011511 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 1052.6671 | 927.3061 | 754.7959 | 535.1364 | 268.3276 |  | 137 | 117 | 85 | 44 | 35 | [7 empty] | 8.8 | 5.9 | 3.2 | 1.632 | 0.984 |  | 2.9298e-05 | 1.9185 |  | 267.2968 | 218.6952 | 168.7158 | 117.3585 | 64.6235 |  | 1.1997e-05 | 1.9521 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01310032/BNA | 5.1 | 39.4 | 4pipe | 12.6 | 4895 | 0.49 | 118.9 | 10.3 | 0.10127 | 0 | 2210 | 2494.0675 | 0.5 | 118.9 | 10.3 | 0.04394 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 1995.3541 | 1757.7295 | 1430.7325 | 1014.363 | 508.621 |  | 202 | 168 | 133 | 85 | 44 | [7 empty] | 10.3 | 6.4 | 3.2 | 1.8 | 1.008 |  | 4.0195e-05 | 1.8944 |  | 506.667 | 414.5416 | 319.8045 | 222.4557 | 122.4953 |  | 1.3303e-05 | 1.9436 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01312032/BNA | 5.1 | 47.2 | 4pipe | 12.6 | 6436 | 0.64 | 160.7 | 10.6 | 0.18845 | 0 | 2906 | 3279.5295 | 0.66 | 160.7 | 10.6 | 0.078227 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 2623.8121 | 2311.3451 | 1881.3569 | 1333.8474 | 668.8166 |  | 273 | 235 | 174 | 114 | 49 | [7 empty] | 10.6 | 7.2 | 4.2 | 2.4 | 1.4 |  | 4.8291e-05 | 1.8807 |  | 666.2471 | 545.1058 | 420.5303 | 292.5205 | 161.0765 |  | 1.412e-05 | 1.9391 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01314032/BNA | 5.1 | 55.1 | 4pipe | 12.6 | 7978 | 0.8 | 199.5 | 19.1 | 0.3166 | 0 | 3602 | 4064.9914 | 0.81 | 199.5 | 19.1 | 0.12065 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 3252.2701 | 2864.9607 | 2331.9813 | 1653.3318 | 829.0122 |  | 339 | 285 | 218 | 129 | 79 | [7 empty] | 19.1 | 12.3 | 6.4 | 3.432 | 1.992 |  | 5.6281e-05 | 1.8703 |  | 825.8273 | 675.6701 | 521.2561 | 362.5853 | 199.6577 |  | 1.5023e-05 | 1.9341 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01317032/BNA | 5.1 | 66.9 | 4pipe | 12.6 | 10290 | 1.03 | 241.3 | 19.4 | 0.57856 | 0 | 4646 | 5243.1844 | 1.05 | 241.3 | 19.4 | 0.20956 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 4194.9571 | 3695.3841 | 3007.9179 | 2132.5584 | 1069.3056 |  | 410 | 352 | 259 | 158 | 84 | [7 empty] | 19.4 | 13.1 | 7.4 | 4.032 | 2.384 |  | 6.8934e-05 | 1.857 |  | 1065.1975 | 871.5165 | 672.3449 | 467.6825 | 257.5295 |  | 1.6397e-05 | 1.9273 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01320032/BNA | 5.1 | 78.7 | 4pipe | 12.6 | 12602 | 1.26 | 279.6 | 20.9 | 0.94303 | 0 | 5690 | 6421.3774 | 1.28 | 279.6 | 20.9 | 0.32165 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 5137.6441 | 4525.8075 | 3683.8545 | 2611.785 | 1309.599 |  | 475 | 403 | 307 | 199 | 93 | [7 empty] | 20.9 | 13.6 | 7.4 | 4.2 | 2.408 |  | 8.2524e-05 | 1.8454 |  | 1304.5678 | 1067.3629 | 823.4336 | 572.7797 | 315.4013 |  | 1.7821e-05 | 1.9209 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01323032/BNA | 5.1 | 90.6 | 4pipe | 12.6 | 14915 | 1.49 | 321.4 | 21.2 | 1.4196 | 0 | 6734 | 7599.5703 | 1.52 | 321.4 | 21.2 | 0.4674 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 6080.3311 | 5356.2309 | 4359.7911 | 3091.0116 | 1549.8924 |  | 546 | 470 | 348 | 228 | 98 | [7 empty] | 21.2 | 14.4 | 8.4 | 4.8 | 2.8 |  | 9.5587e-05 | 1.8373 |  | 1543.938 | 1263.2094 | 974.5223 | 677.8769 | 373.2731 |  | 1.927e-05 | 1.915 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01328032/BNA | 5.1 | 110.2 | 4pipe | 12.6 | 18769 | 1.88 | 402 | 30 | 2.5146 | 0 | 8473 | 9562.0968 | 1.91 | 402 | 30 | 0.77401 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 7651.4761 | 6740.2699 | 5486.3521 | 3889.7226 | 1950.3814 |  | 683 | 587 | 433 | 272 | 133 | [7 empty] | 30 | 20.3 | 11.6 | 6.432 | 3.784 |  | 0.0001181 | 1.8262 |  | 1942.8884 | 1589.62 | 1226.3369 | 853.0389 | 469.7261 |  | 2.1811e-05 | 1.9056 |  | D15
Build-In Floor | Quatro Canal H13 | QCLF.01330032/BNA | 5.1 | 118.1 | 4pipe | 12.6 | 20310 | 2.03 | 440.3 | 38.8 | 2.9822 | 0 | 9169 | 10347.5587 | 2.07 | 440.3 | 38.8 | 0.93203 | 0 | 0.7711 | 0.8539 | 0.8831 | 0.8587 | 0.7807 |  | 8280 | 7294 | 5936.91 | 4209.14 | 2110.58 |  | 748 | 638 | 481 | 313 | 142 | [7 empty] | 38.8 | 26.2 | 14.8 | 8 | 4.8 |  | 0.00012334 | 1.8241 |  | 2102.47 | 1720.18 | 1327.07 | 923.09 | 508.319 |  | 2.4628e-05 | 1.8911 |  | D15
Build-In Floor | Clima Canal H19 | CCLF.01910534/BNA | 7.5 | 41.3 | 2pipe | 13.4 | 8812 | 0.88 | 206.6 | 15 | 0.37065 | 0 | 3543 | 3998.4077 | 0.8 | 206.6 | 15 | 0.30632 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 3592.5601 | 3101.798 | 2566.6888 | 1965.4501 | 1245.4048 |  | 351 | 309 | 236 | 167 | 97 | [7 empty] | 15 | 9.3 | 4.8 | 2.7 | 1.5 |  | 2.7735e-05 | 2 |  | 776.9572 | 626.2629 | 474.2782 | 320.5405 | 164.0625 |  | 2.7735e-05 | 2 |  | D07
Build-In Floor | Clima Canal H19 | CCLF.01912034/BNA | 7.5 | 47.2 | 2pipe | 13.4 | 10950 | 1.1 | 236 | 24 | 0.60091 | 0 | 4402 | 4967.8213 | 0.99 | 236 | 24 | 0.48673 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 4464.1279 | 3854.3052 | 3189.3766 | 2442.2752 | 1547.5444 |  | 401 | 351 | 260 | 179 | 82 | [7 empty] | 24 | 18.4 | 12.1 | 6.7 | 3.2 |  | 2.8777e-05 | 2 |  | 965.4498 | 778.1965 | 589.3398 | 398.3048 | 203.8646 |  | 2.8777e-05 | 2 |  | D07
Build-In Floor | Clima Canal H19 | CCLF.01920034/BNA | 7.5 | 78.7 | 2pipe | 13.4 | 21379 | 2.14 | 442.6 | 38.9 | 2.6573 | 0 | 8595 | 9699.7783 | 1.94 | 442.6 | 38.9 | 2.1838 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 8715.6783 | 7525.072 | 6226.878 | 4768.2517 | 3021.3962 |  | 752 | 660 | 496 | 346 | 179 | [7 empty] | 38.9 | 27.7 | 16.9 | 9.4 | 4.6 |  | 3.3623e-05 | 2 |  | 1884.9257 | 1519.336 | 1150.6158 | 777.6427 | 398.0214 |  | 3.3623e-05 | 2 |  | D07
Build-In Floor | Clima Canal H19 | CCLF.01928034/BNA | 7.5 | 110.2 | 2pipe | 13.4 | 31808 | 3.18 | 649.2 | 53.8 | 6.5992 | 0 | 12788 | 14431.7353 | 2.89 | 649.2 | 53.8 | 5.4505 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 12967.2286 | 11195.8388 | 9264.3795 | 7094.2281 | 4495.248 |  | 1103 | 969 | 732 | 513 | 276 | [7 empty] | 53.8 | 37 | 21.7 | 12.1 | 6.1 |  | 3.7815e-05 | 2 |  | 2804.4017 | 2260.4755 | 1711.8917 | 1156.9806 | 592.1781 |  | 3.7815e-05 | 2 |  | D07
Build-In Floor | Quatro Canal H19 | QCAF.01910534/BNA | 7.5 | 41.3 | 4pipe | 13.4 | 5875 | 0.59 | 206.6 | 15 | 0.13237 | 0 | 3221 | 3635.0187 | 0.73 | 206.6 | 15 | 0.60758 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 2395.04 | 2067.8653 | 1711.1258 | 1310.3 | 830.2699 |  | 351 | 309 | 236 | 167 | 97 | [7 empty] | 15 | 9.3 | 4.8 | 2.7 | 1.5 |  | 2.2035e-05 | 2 |  | 706.3247 | 569.3299 | 431.162 | 291.4005 | 149.1477 |  | 6.6066e-05 | 2 |  | D07
Build-In Floor | Quatro Canal H19 | QCAF.01912034/BNA | 7.5 | 47.2 | 4pipe | 13.4 | 7300 | 0.73 | 236 | 24 | 0.22052 | 0 | 4002 | 4516.4064 | 0.9 | 236 | 24 | 1.0029 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 2976.0853 | 2569.5368 | 2126.251 | 1628.1835 | 1031.6963 |  | 401 | 351 | 260 | 179 | 82 | [7 empty] | 24 | 18.4 | 12.1 | 6.7 | 3.2 |  | 2.3979e-05 | 2 |  | 877.6816 | 707.4513 | 535.7634 | 362.0953 | 185.3315 |  | 7.1743e-05 | 2 |  | D07
Build-In Floor | Quatro Canal H19 | QCAF.01920034/BNA | 7.5 | 78.7 | 4pipe | 13.4 | 14253 | 1.43 | 442.6 | 38.9 | 1.1655 | 0 | 7814 | 8818.3907 | 1.76 | 442.6 | 38.9 | 5.2677 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 5810.4522 | 5016.7146 | 4151.252 | 3178.8344 | 2014.2641 |  | 752 | 660 | 496 | 346 | 179 | [7 empty] | 38.9 | 27.7 | 16.9 | 9.4 | 4.6 |  | 3.3026e-05 | 2 |  | 1713.5688 | 1381.2145 | 1046.0143 | 706.9479 | 361.8376 |  | 9.8543e-05 | 2 |  | D07
Build-In Floor | Quatro Canal H19 | QCAF.01928034/BNA | 7.5 | 110.2 | 4pipe | 13.4 | 21205 | 2.12 | 649.2 | 53.8 | 3.2195 | 0 | 11626 | 13120.3749 | 2.62 | 649.2 | 53.8 | 14.5742 | 0 | 0.9111 | 0.895 | 0.882 | 0.8775 | 0.8766 |  | 8644.8191 | 7463.8925 | 6176.253 | 4729.4854 | 2996.832 |  | 1103 | 969 | 732 | 513 | 276 | [7 empty] | 53.8 | 37 | 21.7 | 12.1 | 6.1 |  | 4.1509e-05 | 2 |  | 2549.4561 | 2054.9777 | 1556.2652 | 1051.8006 | 538.3438 |  | 0.00012303 | 2 |  | D07

## Micro Canal
Selection Model 2022-10 | [44 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF | [35 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF | [15 empty] | h(mm) | 0 | [18 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF | [15 empty] | cf_h | 1 | [18 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF | [36 empty] | -10
[7 empty] | Fanspeed | 100% |  |  |  | *Sound pressure with an assumed room damping of 8dB(A) | [33 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º | [5 empty] | N-Waarde | [5 empty] | 75/65/20ºC | [5 empty] | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  | 16/18/27ºC
Group | Model | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | a | b | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | SalesGroup | JagaSourceCode Stnd
Build-In Floor | Micro Canal | MIRF.00606014/SSS | 2.4 | 23.6 | 2pipe | 5.5 | 957 | 0.1 | 17.2 | 1.6 | 0.00037196 | 18 | 1 | [5 empty] | 390 | [5 empty] | 29.3 | [5 empty] | 18 | [5 empty] | 1.6 | [5 empty] | 2.6466e-05 | 1.1969 | [7 empty] | D05 | MIRF.00606014/SSS
Build-In Floor | Micro Canal | MIRF.00609514/SSS | 2.4 | 37.4 | 2pipe | 5.5 | 1913 | 0.19 | 34.4 | 1.9 | 0.03497 | 21 | 1 | [5 empty] | 780 | [5 empty] | 58.5 | [5 empty] | 21 | [5 empty] | 1.9 | [5 empty] | 0.00015111 | 1.737 | [7 empty] | D05 | MIRF.00609514/SSS
Build-In Floor | Micro Canal | MIRF.00613014/SSS | 2.4 | 51.2 | 2pipe | 5.5 | 2870 | 0.29 | 51.8 | 2.2 | 0.091997 | 22.8 | 1 | [5 empty] | 1170 | [5 empty] | 88 | [5 empty] | 22.8 | [5 empty] | 2.2 | [5 empty] | 0.00010995 | 1.8685 | [7 empty] | D05 | MIRF.00613014/SSS
Build-In Floor | Micro Canal | MIRF.00616514/SSS | 2.4 | 65 | 2pipe | 5.5 | 3827 | 0.38 | 68.9 | 3.1 | 0.061258 | 24 | 1 | [5 empty] | 1560 | [5 empty] | 117 | [5 empty] | 24 | [5 empty] | 3.1 | [5 empty] | 2.6168e-06 | 2.5025 | [7 empty] | D05 | MIRF.00616514/SSS
Build-In Floor | Micro Canal | MIRF.00620014/SSS | 2.4 | 78.7 | 2pipe | 5.5 | 4783 | 0.48 | 86.2 | 3.5 | 0.38934 | 25 | 1 | [5 empty] | 1950 | [5 empty] | 146.5 | [5 empty] | 25 | [5 empty] | 3.5 | [5 empty] | 0.00030694 | 1.7565 | [7 empty] | D05 | MIRF.00620014/SSS

## Unit Heater
Selection Model 2022-10 | [44 empty] | opgave Dries 2018-07-11
|  |  | scroll/ input for corrections: |  |  |  | Entering T | 140 | EWT ºF | [35 empty] | aanv | 16 | ºC
|  |  | Altitude in ft |  |  |  | Return T | 120 | LWT ºF | [15 empty] | h(mm) | 0 | [18 empty] | retour | 18 | ºC
Imperial |  |  | 1 |  |  | % | Return Air T | 65 | AT ºF | [15 empty] | cf_h | 1 | [18 empty] | ruimte | 27 | ºC
[7 empty] | Mean T | 130 | ºF | [36 empty] | -10
* Unit heaters 021 031 221 and 231 can be provided with a 115V motor.
| Electric Consumption differs from the 208V models. | [5 empty] | Fanspeed | 100% |  |  |  | *Sound pressure at 5m¹ from source | [33 empty] | sensible cooling
LA/2022-10-12 |  |  | Height/Depth | Length |  | Width | 140/120/65º | [5 empty] | N-Waarde | [5 empty] | 75/65/20ºC | [5 empty] | AirFlow | [5 empty] | Sound Pressure dB(A) | [5 empty] | P_elek | [5 empty] | Pessure Drop |  |  | 16/18/27ºC
Group | Model * | Product Code | H in inch | L in inch | Type | D in inch | Heating in BTU/h | Flow in GPM | Airflow in CFM | Electrical Consumption W | Water side pressure drop ftH2O | Sound pressure * [dB(A)] | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | KV | hydraulic pressure drop kPa | Kolom | 100% | 80% | 60% | 40% | 20% | Kolom | SalesGroup | JagaSourceCode Stnd
Ceiling/ Wall | Unit Heater (208V) | UNIT.021/EC | 16.1 | 16.1 | 2pipe | 16.9 | 17907 | 1.79 | 837 | 76 | 0.43333 | 44 | 1 | 1 | 1 | 1 | 1 |  | 7300 | 7100 | 6400 | 5500 | 4500 |  | 1422 | 1325 | 1144 | 847 | 594 |  | 44 | 43 | 35 | 28 | 24 |  | 76 | 63 | 43 | 20 | 10 |  | 3.574 | 1.294
Ceiling/ Wall | Unit Heater (208V) | UNIT.031/EC | 16.1 | 16.1 | 2pipe | 16.9 | 23548 | 2.35 | 790 | 79 | 0.37421 | 45 | 1 | 1 | 1 | 1 | 1 |  | 9600 | 9000 | 8100 | 6500 | 5300 |  | 1342 | 1251 | 1080 | 799 | 561 |  | 45 | 44 | 36 | 29 | 25 |  | 79 | 65 | 45 | 21 | 11 |  | 5.0491 | 1.1174
Ceiling/ Wall | Unit Heater (208V) | UNIT.121/EC | 20.9 | 20.9 | 2pipe | 18.9 | 38511 | 3.85 | 1426 | 115 | 2.3888 | 53 | 1 | 1 | 1 | 1 | 1 |  | 15700 | 14600 | 13000 | 10700 | 8000 |  | 2422 | 1984 | 1438 | 997 | 699 |  | 53 | 49 | 41 | 34 | 30 |  | 115 | 80 | 35 | 14 | 8 |  | 3.274 | 7.1333
Ceiling/ Wall | Unit Heater (208V) | UNIT.131/EC | 20.9 | 20.9 | 2pipe | 18.9 | 49304 | 4.93 | 1345 | 118 | 2.2918 | 54 | 1 | 1 | 1 | 1 | 1 |  | 20100 | 19300 | 16700 | 12200 | 9200 |  | 2286 | 1872 | 1357 | 941 | 660 |  | 54 | 50 | 42 | 35 | 31 |  | 118 | 82 | 37 | 15 | 9 |  | 4.2802 | 6.8434
Ceiling/ Wall | Unit Heater (208V) | UNIT.221/EC | 25.6 | 25.6 | 2pipe | 19.6 | 74570 | 7.46 | 2733 | 248 | 2.169 | 57 | 1 | 1 | 1 | 1 | 1 |  | 30400 | 28600 | 26400 | 21700 | 18000 |  | 4643 | 4153 | 3467 | 2517 | 1773 |  | 57 | 51 | 44 | 37 | 32 |  | 248 | 187 | 115 | 54 | 27 |  | 6.6576 | 6.4767
Ceiling/ Wall | Unit Heater (208V) | UNIT.231/EC | 25.6 | 25.6 | 2pipe | 19.6 | 90023 | 9 | 2579 | 251 | 1.5041 | 59 | 1 | 1 | 1 | 1 | 1 |  | 36700 | 34600 | 31100 | 25900 | 21200 |  | 4382 | 3920 | 3272 | 2375 | 1673 |  | 59 | 53 | 46 | 39 | 34 |  | 251 | 189 | 117 | 55 | 28 |  | 9.6453 | 4.4912
Ceiling/ Wall | Unit Heater (208V) | UNIT.321/EC | 30.3 | 30.3 | 2pipe | 22.5 | 98609 | 9.86 | 2893 | 232 | 1.2892 | 52 | 1 | 1 | 1 | 1 | 1 |  | 40200 | 39200 | 36000 | 29100 | 22500 |  | 4915 | 4254 | 2998 | 2036 | 1403 |  | 52 | 44 | 37 | 32 | 28 |  | 232 | 158 | 69 | 34 | 20 |  | 11.4138 | 3.8495
Ceiling/ Wall | Unit Heater (208V) | UNIT.331/EC | 30.3 | 30.3 | 2pipe | 22.5 | 126818 | 12.68 | 2730 | 235 | 1.4919 | 54 | 1 | 1 | 1 | 1 | 1 |  | 51700 | 44800 | 35600 | 27900 | 24800 |  | 4639 | 4015 | 2829 | 1922 | 1324 |  | 54 | 46 | 38 | 33 | 29 |  | 235 | 160 | 71 | 35 | 21 |  | 13.6443 | 4.455
Ceiling/ Wall | Unit Heater (208V) | UNIT.421/EC | 35 | 35 | 2pipe | 21.7 | 159933 | 15.99 | 4795 | 569 | 5.126 | 57 | 1 | 1 | 1 | 1 | 1 |  | 65200 | 53600 | 44200 | 35100 | 29700 |  | 8147 | 6004 | 4344 | 3107 | 2207 |  | 57 | 48 | 42 | 38 | 34 |  | 569 | 249 | 113 | 54 | 30 |  | 9.2824 | 15.3068
Ceiling/ Wall | Unit Heater (208V) | UNIT.431/EC | 35 | 35 | 2pipe | 21.7 | 192802 | 19.28 | 4526 | 572 | 2.5121 | 58 | 1 | 1 | 1 | 1 | 1 |  | 78600 | 65400 | 53600 | 41600 | 32300 |  | 7689 | 5666 | 4100 | 2932 | 2083 |  | 58 | 49 | 44 | 39 | 36 |  | 572 | 251 | 115 | 55 | 31 |  | 15.9879 | 7.5014